## Templates
Templates combine standards and prototype data to create space types and construction sets, templates for each building type are exported to OSM format
0 | 1
Name | Notes
DOE Ref Pre-1980 | Numbers taken from the DOE Pre-1980 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
DOE Ref 1980-2004 | Numbers taken from the DOE 1980-2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
90.1-2004 | Numbers taken from the DOE 2004 reference buildings, with values mapped back to the original data source (standards, etc) where possible. The infiltration numbers were taken from the reference buildings but converted to cfm/ft^2 of exterior surface area. Color scheme is based on redder for more public spaces, bluer for more private spaces. Occupancy from ventilation standards was not used by reference buildings because numbers were generally found to be too high for modeling, representing very conservative design scenarios.
189.1-2009 | Lighting, equipment, infiltration, and ventilation taken from the EnergyPlus example file generator low-energy case. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2007 | Lighting and ventilation taken from 90.1-2007. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2010 | Lighting and ventilation taken from 90.1-2010. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-2013 | Lighting and ventilation taken from 90.1-2013. Equipment and infiltration taken from 189.1-2009 template. Schedules and occupancy taken from DOE Ref 2004 template.
90.1-PRM-2019 | Appendix G Performance Rating Method application of ASHRAE 90.1
ICC IECC 2015 | International Code Council 2015 International Energy Conservation Code
OEESC 2014 | Oregon Efficiency Energy Specialty Code (created by modifying copy of 90.1 2013). Lighting came from Tables 505.5.2(a) and (b) in the 2014 Oregon Energy Efficiency Specialty Code
NREL ZNE Ready 2017 | National Renewable Energy Laboratory Zero Net Energy Ready 2017
ZE AEDG Multifamily | Zero Energy Advanced Energy Design Guide for Multifamily Buildings

## Standards
Standards are actual standards documents issued by a standards organization
Name
AIA 2001
ASHRAE 169-2006
ASHRAE 169-2013
ASHRAE 189.1-2009
ASHRAE 62.1-1999
ASHRAE 62.1-2004
ASHRAE 62.1-2007
ASHRAE 90.1-1999
ASHRAE 90.1-2001
ASHRAE 90.1-2004
ASHRAE 90.1-2007
ASHRAE 90.1-2010
ASHRAE 90.1-2013
GGHC v2.2
ICC IECC 2015

## Prototype Inputs
Each row contains the inputs for a specific building type/climate zone/vintage combination
[16 empty] | PSZAC has different operation schedule | [59 empty] | Gas;Electric | ConstantVolume | OnOff;Continuous
Template | Building Type | HVAC System | Geometry OSM | HVAC JSON | CHW Pumping Type | Chiller Cooling Type | Chiller Condenser Type | Chiller Compressor Type | Chiller Capacity Guess (Tons) | PSZAC Cooling Type | PSZAC Heating Type | PSZAC Fan Type | PSZAC Supplemental Heating Type | PSZAC Operation Schedule | PSZAC OA Damper Schedule | PSZAC Operation Schedule 2 | PSZAC OA Damper Schedule 2 | PSZAC Operation Schedule 3 | PSZAC OA Damper Schedule 3 | Occ Sensing Exterior Lighting Power (W) | Occ Sensing Exterior Lighting Schedule | NonDimming Exterior Lighting Power (W) | NonDimming Exterior Lighting Schedule | Exterior Fuel Equipment1 Power (W) | Exterior Fuel Equipment1 Schedule | Exterior Fuel Equipment2 Power (W) | Exterior Fuel Equipment2 Schedule | Main Water Heater Volume (gal) | Main Water Heater Fuel | Main Water Heater Capacity (Btu/hr) | Main Service Water Temperature (F) | Main Service Water FlowRate Schedule | Main Water Heater Space Name | Main Service Water Peak FlowRate (gal/min) | Main Off Cycle Parasitic Heat Fraction to Tank | Other Off Cycle Parasitic Heat Fraction to Tank | Main Water Use Temperature (F) | Main Service Water Temperature at Fixture (F) | Main Service Water Pump Head (Pa) | Main Service Water Pump Motor Efficiency (%) | Main Service Water Parasitic Fuel Consumption Rate (Btu/h) | Laundry Water Heater Volume (gal) | Laundry Water Heater Fuel | Laundry Water Heater Capacity (Btu/hr) | Laundry Service Water Temperature (F) | Laundry Service Water FlowRate Schedule | Laundry Service Water Peak FlowRate (gal/min) | Laundry Water Use Temperature (F) | Laundry Service Water Temperature at Fixture (F) | Laundry Service Water Pump Head (Pa) | Laundry Service Water Pump Motor Efficiency (%) | Laundry Service Water Parasitic Fuel Consumption Rate (Btu/h) | Booster Water Heater Volume (gal) | Booster Water Heater Fuel | Booster Water Heater Capacity (Btu/hr) | Booster Inlet Water Temperature (F) | Booster Service Water FlowRate Schedule | Booster Water Heater Space Name | Booster Service Water Peak FlowRate (gal/min) | Booster Water Use Temperature (F) | Booster Water Temperature (F) | Booster Service Water Parasitic Fuel Consumption Rate (Btu/h) | Typical Heating Setpoint | Typical Cooling Setpoint | PTAC Cooling Type | PTAC Heating Type | PTAC Fan Type | PTAC Operation Schedule | PTAC OA Damper Schedule | SAC Cooling Type | SAC Heating Type | SAC Fan Type | SAC Operation Schedule | SAC Operation Schedule Meeting | SAC OA Damper Schedule | UnitHeater Heating Type | UnitHeater Fan Type | UnitHeater Fan Control Type | UnitHeater Fan Static Pressure (inH20) | UnitHeater Operation Schedule | VAV Operation Schedule | VAV OA Damper Schedule | VAV Fan Efficiency | VAV Fan Pressure Rise (Pa) | VAV Fan Motor Efficiency | DOAS Fan Maximum Flow Rate (cfm) | DOAS OA Damper Schedule | DOAS Economizer Control Type | Elevator Type | Number of Elevators | Elevator Schedule | Elevator Fan Schedule | Nonmetal Framing (%) | CRAC Cooling Type | CRAC Fan Type | CRAC Operation Schedule | CRAC OA Damper Schedule
90.1-2004 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4546.1674 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4546.1674 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4546.1674 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4327.7903 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
DOE Ref 1980-2004 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4327.7903 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | College |  | ASHRAECollege.osm | ASHRAECollege.json | var_pri | WaterCooled |  | Centrifugal | [19 empty] | 600 | Natural Gas | 200000 | 140 | College BLDG_SWH_SCH | CB_UTILITY_F1 |  |  |  | 110 | 110 |  |  | 4546.1674 | [12 empty] | Electricity | [8 empty] | College HTGSETP_SCH | College CLGSETP_SCH | [16 empty] | College HVACOperationSchd | College MinOA_MotorizedDamper_Sched |  |  |  |  | College MinOA_MotorizedDamper_Sched |  | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [14 empty] | Courthouse Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 4718.796 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [12 empty] | Courthouse Exterior_lighting_schedule_b |  | Courthouse Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 4718.796 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [12 empty] | Courthouse Exterior_lighting_schedule_b |  | Courthouse Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 3594.0774 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [12 empty] | Courthouse Exterior_lighting_schedule_b |  | Courthouse Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 4357.124 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
DOE Ref 1980-2004 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [14 empty] | Always On |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 4357.124 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | Courthouse |  | ASHRAECourthouse.osm | ASHRAECourthouse.json | const_pri_var_sec | WaterCooled |  | Centrifugal | [14 empty] | Always On |  |  |  |  | 100 | Natural Gas | 150000 | 140 | Courthouse BLDG_SWH_SCH | ELEC/MECH_FLR_0 |  |  |  | 110 | 110 |  |  | 68.24 | [21 empty] | Courthouse HTGSETP | Courthouse CLGSETP | [16 empty] | Courthouse HVACOperationSched | Courthouse_MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | ASHRAE9012004FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 3695.1 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  |  |  | 140 | 131 | 29891 | 0.3 | 3594.0774 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH | Kitchen | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | ASHRAE9012007FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 3695.1 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  |  |  | 140 | 131 | 29891 | 0.3 | 3594.0774 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH | Kitchen | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | ASHRAE9012010FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2297 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  |  |  | 140 | 131 | 29891 | 0.3 | 3389.3489 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH | Kitchen | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | FullServiceRestaurant |  | ASHRAE9012013FullServiceRestaurant.osm | ASHRAE9012013FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2297 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  | 0.8 | 0 | 140 | 131 | 29891 | 0.3 | 3389.3489 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH | Kitchen | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | DOERefFullServiceRestaurant.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 5081 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  |  |  | 120 | 120 | 0.1 | 1 | 68.24 | [16 empty] | Kitchen |  |  |  |  | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | FullServiceRestaurant |  | DOERefPre1980FullServiceRestaurant.osm | DOERefFullServiceRestaurant.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched | [6 empty] | 5081 | RestaurantSitDown Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | RestaurantSitDown BLDG_SWH_SCH | Kitchen |  |  |  | 120 | 120 | 0.1 | 1 | 68.24 | [16 empty] | Kitchen |  |  |  |  | FullServiceRestaurant HtgSetp | FullServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
NREL ZNE Ready 2017 | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | ASHRAE9012013FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2302.49 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 29891 | 0.3 | 2443 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH |  | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | HighriseApartment |  | ASHRAEHighriseApartment.osm | ASHRAEHighriseApartment.json | [5 empty] | Water To Air Heat Pump | Water To Air Heat Pump | Cycling | Electric | Always On | Always On | [6 empty] | 13580 | ApartmentHighRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | ApartmentHighRise APT_DHW_SCH | Ambient Temp Schedule |  |  |  | 140 | 140 | 29891 | 0.3 | 32297.6642 | [47 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | HighriseApartment |  | ASHRAEHighriseApartment.osm | ASHRAEHighriseApartment.json | [5 empty] | Water To Air Heat Pump | Water To Air Heat Pump | Cycling | Electric | Always On | Always On | [6 empty] | 13580 | ApartmentHighRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | ApartmentHighRise APT_DHW_SCH | Ambient Temp Schedule |  |  |  | 140 | 140 | 29891 | 0.3 | 32297.6642 | [47 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS
90.1-2010 | HighriseApartment |  | ASHRAEHighriseApartment.osm | ASHRAEHighriseApartment.json | [5 empty] | Water To Air Heat Pump | Water To Air Heat Pump | Cycling | Electric | Always On | Always On | [6 empty] | 10720 | ApartmentHighRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | ApartmentHighRise APT_DHW_SCH | Ambient Temp Schedule |  |  |  | 140 | 140 | 29891 | 0.3 | 31598.1751 | [47 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | HighriseApartment |  | ASHRAE9012013HighriseApartment.osm | ASHRAEHighriseApartment.json | [5 empty] | Water To Air Heat Pump | Water To Air Heat Pump | Cycling | Electric | Always On | Always On | [6 empty] | 10720 | ApartmentHighRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | ApartmentHighRise APT_DHW_SCH | Ambient Temp Schedule |  | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 31598.1751 | [47 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | Hospital |  | ASHRAEHospital.osm | ASHRAE90120042007Hospital.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 16636 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 1295.2 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 |  |  | 140 | 140 | 29891 | 0.3 | 69238.3665 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1389.42 | 0.95 |  |  |  | Traction | 8
90.1-2007 | Hospital |  | ASHRAEHospital.osm | ASHRAE90120042007Hospital.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 16636 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 1295.2 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 |  |  | 140 | 140 | 29891 | 0.3 | 69238.3665 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1389.42 | 0.95 |  |  |  | Traction | 8
90.1-2010 | Hospital |  | ASHRAEHospital.osm | ASHRAE90120102013Hospital.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 13506 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 847.2 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 |  |  | 140 | 140 | 29891 | 0.3 | 68368.2703 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1389.42 | 0.95 |  |  |  | Traction | 8
90.1-2013 | Hospital |  | ASHRAE9012013Hospital.osm | ASHRAE90120102013Hospital.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 13506 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 501 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 68368.2703 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1389.42 | 0.95 |  |  |  | Traction | 8
DOE Ref 1980-2004 | Hospital |  | ASHRAEHospital.osm | DOERefHospital.json | const_pri | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 21874 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 847.2 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 |  |  | 140 | 140 | 29891 | 0.3 | 10024 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 8
DOE Ref Pre-1980 | Hospital |  | ASHRAEHospital.osm | DOERefHospital.json | const_pri | WaterCooled |  | Centrifugal | 250 | Water | Water | ConstantVolume | Electricity | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | [6 empty] | 21874 | Hospital Exterior_Lgt_ALWAYS_ON | 162962.637 | Hospital BLDG_ELEVATORS | 847.2 | Hospital ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | Hospital BLDG_SWH_SCH | Basement | 7.63 |  |  | 140 | 140 | 29891 | 0.3 | 10024 | 300 | Natural Gas | 300000 | 180 | Hospital LAUNDRY_SWH_SCH | 2.8 | 180 | 180 |  |  | 0 | 6 | Electricity | 10236 |  | Hospital BLDG_SWH_SCH | KITCHEN_FLR_5 | 0.58 | 180 | 180 | 0 | Hospital Bldg HtgSetp | Hospital Bldg ClgSetp | [16 empty] | Hospital HVACOperationSchd | Hospital BLDG_OA_FRAC_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Traction | 8
90.1-2004 | LargeDataCenterHighITE |  | ASHRAELargeDataCenterHighITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 1000 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2007 | LargeDataCenterHighITE |  | ASHRAELargeDataCenterHighITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 1000 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2010 | LargeDataCenterHighITE |  | ASHRAELargeDataCenterHighITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 1000 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2013 | LargeDataCenterHighITE |  | ASHRAELargeDataCenterHighITE.osm | ASHRAE2013LargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 1000 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2004 | LargeDataCenterLowITE |  | ASHRAELargeDataCenterLowITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2007 | LargeDataCenterLowITE |  | ASHRAELargeDataCenterLowITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2010 | LargeDataCenterLowITE |  | ASHRAELargeDataCenterLowITE.osm | ASHRAELargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2013 | LargeDataCenterLowITE |  | ASHRAELargeDataCenterLowITE.osm | ASHRAE2013LargeDataCenter.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 250 | [53 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [16 empty] | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2004 | LargeHotel |  | ASHRAE90120042007LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [12 empty] | 19478 | Always On | 122221.978 | HotelLarge BLDG_ELEVATORS | 971.4 | HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | Basement |  |  |  | 140 | 110 | 29891 | 0.3 | 63695.9561 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH | KITCHEN_FLR_6 | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2007 | LargeHotel |  | ASHRAE90120042007LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [12 empty] | 19478 | Always On | 122221.978 | HotelLarge BLDG_ELEVATORS | 971.4 | HotelLarge ELEV_LIGHT_FAN_SCH_24_7 | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | Basement |  |  |  | 140 | 110 | 29891 | 0.3 | 63695.9561 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH | KITCHEN_FLR_6 | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2010 | LargeHotel |  | ASHRAE9012010LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [12 empty] | 15666 | Always On | 122221.978 | HotelLarge BLDG_ELEVATORS | 635.4 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | Basement |  |  |  | 140 | 110 | 29891 | 0.3 | 63013.5277 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH | KITCHEN_FLR_6 | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2013 | LargeHotel |  | ASHRAE9012013LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [12 empty] | 15666 | Always On | 122221.978 | HotelLarge BLDG_ELEVATORS | 375.9 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch | Basement |  | 0.8 | 0 | 140 | 110 | 29891 | 0.3 | 63013.5277 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH | KITCHEN_FLR_6 | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
DOE Ref 1980-2004 | LargeHotel |  | DOERefLargeHotel.osm | DOERefLargeHotel.json | const_pri | AirCooled | WithCondenser |  | 310 | [10 empty] | 27826 | Always On |  |  | 122221.978 | LargeHotel BLDG ELEVATORS |  |  | 528 | Natural Gas | 2883000 | 140 | HotelLarge BLDG_SWH_SCH | Basement |  |  |  | 110 | 110 | 179352 | 0.3 | 7851.34 | [16 empty] | KITCHEN_FLR_6 | [22 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.945 | 4346.2446 | HotelLarge MinOA_Sched | NoEconomizer | Traction | 6
DOE Ref Pre-1980 | LargeHotel |  | DOERefLargeHotel.osm | DOERefLargeHotel.json | const_pri | AirCooled | WithCondenser |  | 310 | [10 empty] | 27826 | Always On |  |  | 122221.978 | LargeHotel BLDG ELEVATORS |  |  | 528 | Natural Gas | 2883000 | 140 | HotelLarge BLDG_SWH_SCH | Basement |  |  |  | 110 | 110 | 179352 | 0.3 | 7851.34 | [16 empty] | KITCHEN_FLR_6 | [22 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.945 | 4346.2446 | HotelLarge MinOA_Sched | NoEconomizer | Traction | 6
NREL ZNE Ready 2017 | LargeHotel |  | ASHRAE9012013LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 14952 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 375.9 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch |  |  |  |  | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH |  | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
90.1-2004 | LargeOffice |  | ASHRAELargeOffice.osm | ASHRAELargeOffice.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | [6 empty] | 62782.82 | Always On | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 28582.0804 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2007 | LargeOffice |  | ASHRAELargeOffice.osm | ASHRAELargeOffice.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | [6 empty] | 62782.82 | Always On | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 28582.0804 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2010 | LargeOffice |  | ASHRAELargeOffice.osm | ASHRAELargeOffice.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43301.5 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 27797.2878 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2013 | LargeOffice |  | ASHRAE9012013LargeOffice.osm | ASHRAELargeOffice.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43301.5 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 752 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.58 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 27797.2878 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
DOE Ref 1980-2004 | LargeOffice |  | DOERefLargeOffice.osm | DOERefLargeOffice.json | const_pri | WaterCooled |  | Centrifugal | 470 | [12 empty] | 61595 | Always On | 244443 | Large Office BLDG ELEVATORS |  |  | 200 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.355 |  |  | 140 | 140 | 179352 | 0.3 | 68.24 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389 | 0.95
DOE Ref Pre-1980 | LargeOffice |  | DOERefLargeOffice.osm | DOERefLargeOffice.json | const_pri | WaterCooled |  | Centrifugal | 470 | [12 empty] | 61595 | Always On | 244443 | Large Office BLDG ELEVATORS |  |  | 200 | Natural Gas | 2883259 | 140 | OfficeLarge BLDG_SWH_SCH | Basement | 0.355 |  |  | 140 | 140 | 179352 | 0.3 | 68.24 | [20 empty] | 0 | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2004 | LargeOfficeDetail |  |  |  | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2007 | LargeOfficeDetail |  |  |  | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2010 | LargeOfficeDetail |  |  |  | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2013 | LargeOfficeDetail |  |  |  | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2004 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2007 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2010 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
90.1-2013 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 43305.0887 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95
DOE Ref 1980-2004 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
DOE Ref Pre-1980 | LargeOfficeDetailed |  | ASHRAELargeOfficeDetailed.osm | ASHRAELargeOfficeDetailed.json | const_pri_var_sec | WaterCooled |  | Centrifugal | 470 | Water | Water | ConstantVolume |  | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched |  |  |  |  | 62787 | OfficeLarge Exterior_lighting_schedule_b | 12979.2 | OfficeLarge Exterior_lighting_schedule_a | 244443.956 | Large Office BLDG ELEVATORS | 1270.8 | OfficeLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 300 | Natural Gas | 300000 | 140 | OfficeLarge BLDG_SWH_SCH |  | 0.58 |  |  | 140 | 140 | 29891 | 0.3 | 9455 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeLarge HVACOperationSchd | OfficeLarge MinOA_MotorizedDamper_Sched | 0.6045 | 1389.32 | 0.93
90.1-2004 | MediumOffice |  | ASHRAEMediumOffice.osm | ASHRAEMediumOffice.json | [17 empty] | 14338.152 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Core_bottom |  |  |  | 140 | 131 | 29891 | 0.3 | 7197.6747 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | MediumOffice |  | ASHRAEMediumOffice.osm | ASHRAEMediumOffice.json | [17 empty] | 14338.152 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Core_bottom |  |  |  | 140 | 131 | 29891 | 0.3 | 7197.6747 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | MediumOffice |  | ASHRAEMediumOffice.osm | ASHRAEMediumOffice.json | [15 empty] | 7402.3 | OfficeMedium Exterior_lighting_schedule_b | 519.2 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Core_bottom |  |  |  | 140 | 131 | 29891 | 0.3 | 6835.9876 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
90.1-2013 | MediumOffice |  | ASHRAE9012013MediumOffice.osm | ASHRAEMediumOffice.json | [15 empty] | 7402.3 | OfficeMedium Exterior_lighting_schedule_b | 519.2 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Core_bottom |  | 0.8 | 0 | 140 | 131 | 29891 | 0.3 | 6835.9876 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
DOE Ref 1980-2004 | MediumOffice |  | ASHRAEMediumOffice.osm | DOERef1980to2004MediumOffice.json | [17 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | Core_bottom |  |  |  | 140 | 110 | 179352 | 0.85 | 68.24 | [21 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [16 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | MediumOffice |  | ASHRAEMediumOffice.osm | DOERefPre1980MediumOffice.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | [6 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | Core_bottom |  |  |  | 140 | 110 | 179352 | 0.85 | 68.24 | [21 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
NREL ZNE Ready 2017 | MediumOffice |  | ASHRAEMediumOffice.osm | ASHRAEMediumOffice.json | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 29891 | 0.3 | 4357.124 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
90.1-2004 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [17 empty] | 14385 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Mechanical_Bot | 0.85 |  |  | 140 | 140 | 29891 | 0.3 | 4718.796 | [21 empty] | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [17 empty] | 14385 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Mechanical_Bot | 0.85 |  |  | 140 | 140 | 29891 | 0.3 | 4718.796 | [21 empty] | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Mechanical_Bot | 0.85 |  |  | 140 | 140 | 29891 | 0.3 | 4357.124 | [21 empty] | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH | Mechanical_Bot | 0.85 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 4357.124 | [21 empty] | OfficeMedium HTGSETP_SCH_NO_OPTIMUM | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
DOE Ref 1980-2004 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [17 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | Mechanical_Bot | 0.4945 |  |  | 140 | 140 | 179352 | 0.85 | 68.24 | [21 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [16 empty] | OfficeMedium VAV Operation | OfficeMedium VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | MediumOfficeDetailed |  | ASHRAEMediumOfficeDetailed.osm | ASHRAEMediumOfficeDetailed.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | [6 empty] | 17809 | OfficeMedium Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 2883000 | 140 | Medium Office Bldg Swh | Mechanical_Bot | 0.4945 |  |  | 140 | 140 | 179352 | 0.85 | 68.24 | [21 empty] | Medium Office HtgSetp | Medium Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | MidriseApartment |  | ASHRAEMidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 4642 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 140 | 140 | 0.01 | 1 | 6653.6769 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | MidriseApartment |  | ASHRAEMidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 4642 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 140 | 140 | 0.01 | 1 | 6653.6769 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | MidriseApartment |  | ASHRAEMidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 2508 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 140 | 140 | 0.01 | 1 | 6445.5362 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | MidriseApartment |  | ASHRAE9012013MidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 2508 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  | 0 | 0 | 140 | 140 | 0.01 | 1 | 6445.5362 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
DOE Ref 1980-2004 | MidriseApartment |  | DOERefMidriseApartment.osm | DOERefMidriseApartment.json | [17 empty] | 6436 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1 | Natural Gas | 721668 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 110 | 110 | 0.01 | 1 | 6.82 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Electric | ConstantVolume | Continuous | 0.2 | Always On | [8 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | MidriseApartment |  | DOERefMidriseApartment.osm | DOERefMidriseApartment.json | [17 empty] | 6436 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1 | Natural Gas | 721668 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 110 | 110 | 0.01 | 1 | 6.82 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | Electric | ConstantVolume | Continuous | 0.2 | Always On | [8 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
NREL ZNE Ready 2017 | MidriseApartment |  | ASHRAEMidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 2553 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 140 | 140 | 0.01 | 1 | 87.75 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | Outpatient |  | ASHRAEOutpatient.osm | ASHRAEOutpatient.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | [12 empty] | 14442 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  |  |  | 140 | 140 | 29891 | 0.3 | 26067.4341 | [21 empty] | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
90.1-2007 | Outpatient |  | ASHRAEOutpatient.osm | ASHRAEOutpatient.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | [12 empty] | 14442 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  |  |  | 140 | 140 | 29891 | 0.3 | 26067.4341 | [21 empty] | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
90.1-2010 | Outpatient |  | ASHRAEOutpatient.osm | ASHRAEOutpatient.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | [10 empty] | 8297.7 | OutPatientHealthCare Exterior_lighting_schedule_b | 173.8 | OutPatientHealthCare Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  |  |  | 140 | 140 | 29891 | 0.3 | 25640.9164 | [21 empty] | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
90.1-2013 | Outpatient |  | ASHRAE9012013Outpatient.osm | ASHRAEOutpatient.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | [10 empty] | 8297.7 | OutPatientHealthCare Exterior_lighting_schedule_b | 173.8 | OutPatientHealthCare Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 25640.9164 | [21 empty] | OutPatientHealthCare HTGSETP_SCH_NO_OPTIMUM | OutPatientHealthCare CLGSETP_SCH_NO_SETBACK | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
DOE Ref 1980-2004 | Outpatient |  | ASHRAEOutpatient.osm | DOERefOutpatient.json | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 16951 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  |  |  | 110 | 110 | 179352 | 0.9 | 68.24 | [21 empty] | Outpatient HtgSetp | Outpatient ClgSetp | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH_Pre2004 | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
DOE Ref Pre-1980 | Outpatient |  | ASHRAEOutpatient.osm | DOERefOutpatient.json | const_pri | AirCooled | WithCondenser |  | 470 | [12 empty] | 16951 | OutPatientHealthCare Exterior_Lgt_ALWAYS_ON |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | OutPatientHealthCare BLDG_SWH_SCH | Floor 3 Mechanical |  |  |  | 110 | 110 | 179352 | 0.9 | 68.24 | [21 empty] | Outpatient HtgSetp | Outpatient ClgSetp | [16 empty] | OutPatientHealthCare HVACOperationSchd | OutPatientHealthCare BLDG_OA_SCH_Pre2004 | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 3
90.1-2004 | PrimarySchool |  | ASHRAEPrimarySchool.osm | ASHRAEPrimarySchool.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | [6 empty] | 5297.718 | SchoolPrimary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 1.7 |  |  | 140 | 140 | 29891 | 0.3 | 3635.6032 | [11 empty] | 6 | Electricity | 20473 |  | SchoolPrimary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 1 | 180 | 180 | 0 | [18 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | PrimarySchool |  | ASHRAEPrimarySchool.osm | ASHRAEPrimarySchool.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | [6 empty] | 5297.718 | SchoolPrimary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 1.7 |  |  | 140 | 140 | 29891 | 0.3 | 3635.6032 | [11 empty] | 6 | Electricity | 20473 |  | SchoolPrimary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 1 | 180 | 180 | 0 | [18 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | PrimarySchool |  | ASHRAEPrimarySchool.osm | ASHRAEPrimarySchool.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched |  |  |  |  | 3231.4 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 1.7 |  |  | 140 | 140 | 29891 | 0.3 | 3434.2868 | [11 empty] | 6 | Electricity | 20473 |  | SchoolPrimary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 1 | 180 | 180 | 0 | [18 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | PrimarySchool |  | ASHRAE9012013PrimarySchool.osm | ASHRAEPrimarySchool.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched |  |  |  |  | 3231.4 | SchoolPrimary Exterior_lighting_schedule_b | 150.48 | SchoolPrimary Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 1.7 | 0.8 | 0 | 140 | 140 | 29891 | 0.3 | 3434.2868 | [11 empty] | 6 | Electricity | 20473 |  | SchoolPrimary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 1 | 180 | 180 | 0 | [18 empty] | SchoolPrimary HVACOperationSchd | SchoolPrimary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | PrimarySchool |  | DOERefPrimarySchool.osm | DOERefPrimarySchool.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper | [6 empty] | 10519 | PrimarySchool Exterior Lights Always On |  |  |  |  | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 2.6 |  |  | 140 | 140 | 1 | 1 | 68.24 | [16 empty] | KITCHEN_ZN_1_FLR_1 | [22 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | PrimarySchool |  | DOERefPrimarySchool.osm | DOERefPrimarySchool.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | PrimarySchool PSZ-AC Operation | PrimarySchool PSZ-AC OA Damper | [6 empty] | 10519 | PrimarySchool Exterior Lights Always On |  |  |  |  | 264 | Natural Gas | 2883259 | 140 | SchoolPrimary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 2.6 |  |  | 140 | 140 | 1 | 1 | 68.24 | [16 empty] | KITCHEN_ZN_1_FLR_1 | [22 empty] | PrimarySchool VAV Operation | PrimarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | ASHRAE9012004QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 1743 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | KITCHEN |  |  |  | 140 | 131 | 0.001 | 0.3 | 2463.5665 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | ASHRAE90120072010QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 1743 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | KITCHEN |  |  |  | 140 | 131 | 0.001 | 0.3 | 2463.5665 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | ASHRAE90120072010QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1034.1 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | KITCHEN |  |  |  | 140 | 131 | 0.001 | 0.3 | 2456.7422 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | QuickServiceRestaurant |  | ASHRAE9012013QuickServiceRestaurant.osm | ASHRAE9012013QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1034.1 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH | KITCHEN |  | 0.8 | 0 | 140 | 131 | 0.001 | 0.3 | 2456.7422 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | DOERefQuickServiceRestaurant.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 2963 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | QuickServiceRestaurant Bldg Swh | KITCHEN |  |  |  | 120 | 120 | 0.1 | 1 | 68.24 | [21 empty] | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | QuickServiceRestaurant |  | DOERefPre1980QuickServiceRestaurant.osm | DOERefQuickServiceRestaurant.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched | [6 empty] | 2963 | RestaurantFastFood Exterior_Lgt_ALWAYS_ON |  |  |  |  | 52.83 | Natural Gas | 2883000 | 140 | QuickServiceRestaurant Bldg Swh | KITCHEN |  |  |  | 120 | 120 | 0.1 | 1 | 68.24 | [21 empty] | QuickServiceRestaurant HtgSetp | QuickServiceRestaurant ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
NREL ZNE Ready 2017 | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | ASHRAE9012013QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1039.09 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 0.001 | 0.3 | 68.24 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | RetailStandalone |  | ASHRAE90120042007RetailStandalone.osm | ASHRAE90120042007RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 7322 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 0 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | Back_space | 0.3 |  |  | 140 | 140 | 0.001 | 0.3 | 6353.4084 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 4.4584 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2007 | RetailStandalone |  | ASHRAE90120042007RetailStandalone.osm | ASHRAE90120042007RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 7322 | RetailStandalone Exterior_Lgt_ALWAYS_ON | 0 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | Back_space | 0.3 |  |  | 140 | 140 | 0.001 | 0.3 | 6353.4084 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 4.4584 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2010 | RetailStandalone |  | ASHRAE9012010RetailStandalone.osm | ASHRAE90120102013RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4328 | RetailStandalone Exterior_lighting_schedule_b | 316 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | Back_space | 0.3 |  |  | 140 | 140 | 0.001 | 0.3 | 6346.5841 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2013 | RetailStandalone |  | ASHRAE9012013RetailStandalone.osm | ASHRAE90120102013RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4328 | RetailStandalone Exterior_lighting_schedule_b | 316 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH | Back_space | 0.3 | 0 | 0 | 140 | 140 | 0.001 | 0.3 | 6346.5841 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
DOE Ref 1980-2004 | RetailStandalone |  | DOERefRetailStandalone.osm | DOERefRetailStandalone.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | [6 empty] | 9995 | Always On | [9 empty] | Back_space | [29 empty] | Retail HtgSetp | Retail ClgSetp | [11 empty] | Electric | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
DOE Ref Pre-1980 | RetailStandalone |  | DOERefRetailStandalone.osm | DOERefRetailStandalone.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched | [6 empty] | 9995 | Always On | [9 empty] | Back_space | [29 empty] | Retail HtgSetp | Retail ClgSetp | [11 empty] | Electric | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
NREL ZNE Ready 2017 | RetailStandalone |  | ASHRAE90120102013RetailStandalone.osm | ASHRAE90120102013RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH |  | 0.3 |  |  | 140 | 140 | 0.001 | 0.3 | 6347 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
90.1-2004 | RetailStripmall |  | ASHRAERetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH |  |  | 10625.3438 | RetailStripmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | [5 empty] | 120 | 131 |  |  | 593.7127 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | RetailStripmall |  | ASHRAERetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH |  |  | 10625.3438 | RetailStripmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | [5 empty] | 120 | 131 |  |  | 593.7127 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | RetailStripmall |  | ASHRAERetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 6630.0233 | RetailStripmall Exterior_lighting_schedule_b | 418.4 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | [5 empty] | 120 | 131 |  |  | 590.3006 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | RetailStripmall |  | ASHRAE9012013RetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 6630.0233 | RetailStripmall Exterior_lighting_schedule_b | 418.4 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 |  |  |  | 0 | 0 | 120 | 131 |  |  | 590.3006 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | RetailStripmall |  | ASHRAERetailStripmall.osm | DOERefRetailStripmall.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched |  |  | 13499 | Always On | [39 empty] | StripMall HtgSetp | StripMall ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | RetailStripmall |  | ASHRAERetailStripmall.osm | DOERefRetailStripmall.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched | Stripmall HVACOperationSchd | Stripmall MinOA_Sched |  |  | 13499 | Always On | [39 empty] | StripMall HtgSetp | StripMall ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
NREL ZNE Ready 2017 | RetailStripmall |  | ASHRAERetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | [5 empty] | 120 | 131 |  |  | 590.3 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
ZE AEDG Multifamily | FullServiceRestaurant |  | ASHRAEFullServiceRestaurant.osm | ASHRAE9012013FullServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantSitDown HVACOperationSchd | RestaurantSitDown MinOA_MotorizedDamper_Sched |  |  |  |  | 2302.49 | RestaurantSitDown Exterior_lighting_schedule_b | 154.01 | RestaurantSitDown Exterior_lighting_schedule_a |  |  |  |  | 200 | Natural Gas | 200000 | 140 | RestaurantSitDown BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 29891 | 0.3 | 2443 | [11 empty] | 6 | Electricity | 27297 |  | RestaurantSitDown BLDG_SWH_SCH |  | 1.33 | 180 | 180 |  | RestaurantSitDown HTGSETP_SCH_NO_OPTIMUM | RestaurantSitDown CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
ZE AEDG Multifamily | LargeHotel |  | ASHRAE9012013LargeHotel.osm | ASHRAELargeHotel.json | const_pri_var_sec | AirCooled | WithCondenser |  | 310 | [10 empty] | 14952 | Always On |  |  | 122221.978 | HotelLarge BLDG_ELEVATORS | 375.9 | HotelLarge ELEV_LIGHT_FAN_SCH_ADD_DF | 600 | Natural Gas | 600000 | 140 | HotelLarge GuestRoom_SWH_Sch |  |  |  |  | 140 | 110 | 29891 | 0.3 | 7851.34 | 300 | Natural Gas | 300000 | 180 | HotelLarge LAUNDRY_SWH_SCH | 30.6 | 180 | 180 |  |  | 0 | 6 | Electricity | 27297 |  | HotelLarge BLDG_SWH_SCH |  | 1.33 | 180 | 180 | 0 | [18 empty] | HotelLarge HVACOperationSchd | HotelLarge MinOA_MotorizedDamper_Sched | 0.6201 | 1389.42 | 0.954 | 4346.2446 | HotelLarge MinOA_Sched | DifferentialDrybulb | Traction | 6
ZE AEDG Multifamily | MediumOffice |  | ASHRAEMediumOffice.osm | ASHRAEMediumOffice.json | [15 empty] | 7476.45 | OfficeMedium Exterior_lighting_schedule_b | 623.03 | OfficeMedium Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | OfficeMedium BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 29891 | 0.3 | 4357.124 | [21 empty] | HTGSETP_SCH_PACU_VAV_bot | OfficeMedium CLGSETP_SCH_NO_SETBACK | [16 empty] | OfficeMedium HVACOperationSchd | OfficeMedium MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF
ZE AEDG Multifamily | MidriseApartment |  | ASHRAEMidriseApartment.osm | ASHRAEMidriseApartment.json | [17 empty] | 2553 | ApartmentMidRise Exterior_Lgt_ALWAYS_ON |  |  |  |  | 1150 | Electricity | 1150000 | 140 | ApartmentMidRise APT_DHW_SCH |  |  |  |  | 140 | 140 | 0.01 | 1 | 87.75 | [28 empty] | Single Speed DX AC | Gas | ConstantVolume | ApartmentMidRise All On |  | ApartmentMidRise COMPACT HVAC-ALWAYS 1 | [13 empty] | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7
ZE AEDG Multifamily | QuickServiceRestaurant |  | ASHRAEQuickServiceRestaurant.osm | ASHRAE9012013QuickServiceRestaurant.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RestaurantFastFood HVACOperationSchd | RestaurantFastFood MinOA_MotorizedDamper_Sched |  |  |  |  | 1039.09 | RestaurantFastFood Exterior_lighting_schedule_b | 122.81 | RestaurantFastFood Exterior_lighting_schedule_a |  |  |  |  | 100 | Natural Gas | 100000 | 140 | RestaurantFastFood BLDG_SWH_SCH |  |  |  |  | 140 | 131 | 0.001 | 0.3 | 68.24 | [21 empty] | RestaurantFastFood HTGSETP_SCH_NO_OPTIMUM | RestaurantFastFood CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
ZE AEDG Multifamily | RetailStandalone |  | ASHRAE90120102013RetailStandalone.osm | ASHRAE90120102013RetailStandalone.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStandalone HVACOperationSchd | RetailStandalone MinOA_MotorizedDamper_Sched |  |  |  |  | 4365.06 | RetailStandalone Exterior_lighting_schedule_b | 379.58 | RetailStandalone Exterior_lighting_schedule_a |  |  |  |  | 40 | Natural Gas | 40000 | 140 | RetailStandalone BLDG_SWH_SCH |  | 0.3 |  |  | 140 | 140 | 0.001 | 0.3 | 6347 | [21 empty] | RetailStandalone HTGSETP_SCH_NO_OPTIMUM | RetailStandalone CLGSETP_SCH_NO_SETBACK | [11 empty] | Gas | ConstantVolume | OnOff | 2.5 | RetailStandalone FrontEntry_FanSched | [9 empty] | 0
ZE AEDG Multifamily | RetailStripmall |  | ASHRAERetailStripmall.osm | ASHRAERetailStripmall.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | RetailStripmall Type1_FAN_SCH | RetailStripmall Type1_MinOA_MotorizedDamper_SCH | RetailStripmall Type2_FAN_SCH | RetailStripmall Type2_MinOA_MotorizedDamper_SCH | RetailStripmall Type3_FAN_SCH | RetailStripmall Type3_MinOA_MotorizedDamper_SCH | 5112.44 | RetailStripmall Exterior_lighting_schedule_b | 334.69 | RetailStripmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | [5 empty] | 120 | 131 |  |  | 590.3 | [21 empty] | RetailStripmall Type1_HTGSETP_SCH_NO_OPTIMUM | RetailStripmall Type1_CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | SecondarySchool |  | ASHRAESecondarySchool.osm | ASHRAESecondarySchool.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | [6 empty] | 13795.252 | SchoolSecondary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.63 |  |  | 140 | 140 | 34026 | 0.3 | 4546.1674 | [11 empty] | 6 | Electricity | 47770 |  | SchoolSecondary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2007 | SecondarySchool |  | ASHRAESecondarySchool.osm | ASHRAESecondarySchool.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | [6 empty] | 13795.252 | SchoolSecondary Exterior_Lgt_ALWAYS_ON |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.63 |  |  | 140 | 140 | 34026 | 0.3 | 4546.1674 | [11 empty] | 6 | Electricity | 47770 |  | SchoolSecondary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2010 | SecondarySchool |  | ASHRAESecondarySchool.osm | ASHRAESecondarySchool.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched |  |  |  |  | 8552 | SchoolSecondary Exterior_lighting_schedule_b | 441.8 | SchoolSecondary Exterior_lighting_schedule_a |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.63 |  |  | 140 | 140 | 34026 | 0.3 | 4327.7903 | [11 empty] | 6 | Electricity | 47770 |  | SchoolSecondary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2013 | SecondarySchool |  | ASHRAE9012013SecondarySchool.osm | ASHRAESecondarySchool.json | const_pri_var_sec | AirCooled | WithCondenser |  | 470 | Two Speed DX AC | Gas | ConstantVolume |  | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched |  |  |  |  | 8552 | SchoolSecondary Exterior_lighting_schedule_b | 441.8 | SchoolSecondary Exterior_lighting_schedule_a |  |  |  |  | 600 | Natural Gas | 600000 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.63 | 0.8 | 0 | 140 | 140 | 34026 | 0.3 | 4327.7903 | [11 empty] | 6 | Electricity | 47770 |  | SchoolSecondary BLDG_SWH_SCH | KITCHEN_ZN_1_FLR_1 | 23.7 | 180 | 180 | [19 empty] | SchoolSecondary HVACOperationSchd | SchoolSecondary MinOA_MotorizedDamper_Sched | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF
DOE Ref 1980-2004 | SecondarySchool |  | DOERefSecondarySchool.osm | DOERef1980to2004SecondarySchool.json | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper | [6 empty] | 21874 | SecondarySchool Exterior Lights Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.18 |  |  | 140 | 140 |  |  | 68.24 | [16 empty] | KITCHEN_ZN_1_FLR_1 | [22 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
DOE Ref Pre-1980 | SecondarySchool |  | DOERefSecondarySchool.osm | DOERefPre1980SecondarySchool.json | const_pri | AirCooled | WithCondenser |  | 470 | Single Speed DX AC | Gas | ConstantVolume |  | SecondarySchool PSZ-AC Operation | SecondarySchool PSZ-AC OA Damper | [6 empty] | 21874 | SecondarySchool Exterior Lights Always On |  |  |  |  | 792 | Natural Gas | 2883259 | 140 | SchoolSecondary BLDG_SWH_SCH | MECH_ZN_1_FLR_1 | 7.18 |  |  | 140 | 140 |  |  | 68.24 | [16 empty] | KITCHEN_ZN_1_FLR_1 | [22 empty] | SecondarySchool VAV Operation | SecondarySchool VAV OA Damper | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7
90.1-2004 | SmallDataCenterHighITE |  | ASHRAESmallDataCenterHighITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2007 | SmallDataCenterHighITE |  | ASHRAESmallDataCenterHighITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2010 | SmallDataCenterHighITE |  | ASHRAESmallDataCenterHighITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2013 | SmallDataCenterHighITE |  | ASHRAESmallDataCenterHighITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2004 | SmallDataCenterLowITE |  | ASHRAESmallDataCenterLowITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2007 | SmallDataCenterLowITE |  | ASHRAESmallDataCenterLowITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2010 | SmallDataCenterLowITE |  | ASHRAESmallDataCenterLowITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2013 | SmallDataCenterLowITE |  | ASHRAESmallDataCenterLowITE.osm | ASHRAESmallDataCenter.json | [58 empty] | DataCenter HTGSETP_SCH | DataCenter CLGSETP_SCH | [29 empty] | Single Speed DX AC | ConstantVolume | DataCenter HVACOperationSchd | DataCenter MinOA_MotorizedDamper_Sched
90.1-2004 | SmallHotel |  | ASHRAESmallHotel.osm | ASHRAESmallHotel.json | [17 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  |  |  | 140 | 140 | 29891 | 0.85 | 28773.6722 | 200 | Natural Gas | 200000 | 180 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 0 | [12 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2007 | SmallHotel |  | ASHRAESmallHotel.osm | ASHRAESmallHotel.json | [17 empty] | 6063 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  |  |  | 140 | 140 | 29891 | 0.85 | 28773.6722 | 200 | Natural Gas | 200000 | 180 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 0 | [12 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2010 | SmallHotel |  | ASHRAESmallHotel.osm | ASHRAESmallHotel.json | [17 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  |  |  | 140 | 140 | 29891 | 0.85 | 28309.6209 | 200 | Natural Gas | 200000 | 180 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 0 | [12 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2013 | SmallHotel |  | ASHRAE9012013SmallHotel.osm | ASHRAESmallHotel.json | [17 empty] | 4188 | HotelSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 300 | Natural Gas | 300000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  | 0.8 | 0 | 140 | 140 | 29891 | 0.85 | 28309.6209 | 200 | Natural Gas | 200000 | 180 | HotelSmall LaundryRoom_SHW_Sch | 2.05 | 180 | 180 | 0.001 | 0.3 | 0 | [12 empty] | Single Speed DX AC | Electric | ConstantVolume | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | Single Speed DX AC | Gas | ConstantVolume | SmallHotel Split-AC Operation | HotelSmall Off During Unoccupied Period | SmallHotel Split-AC OA Damper | Electric | ConstantVolume | Continuous | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
DOE Ref 1980-2004 | SmallHotel |  | DOERefSmallHotel.osm | DOERef1980to2004SmallHotel.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallHotel PSZ-AC Operation | SmallHotel PSZ-AC OA Damper | [6 empty] | 16715 | SmallHotel Exterior Lights |  |  |  |  | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  |  |  | 110 | 110 | 179352 | 0.9 | 68.24 | [23 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [6 empty] | Electric | ConstantVolume | Cycling | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
DOE Ref Pre-1980 | SmallHotel |  | DOERefSmallHotel.osm | DOERefPre1980SmallHotel.json | [17 empty] | 16715 | SmallHotel Exterior Lights |  |  |  |  | 528.3 | Natural Gas | 2883000 | 140 | HotelSmall GuestRoom_SHW_Sch | MECHANICALROOMFLR1 |  |  |  | 110 | 110 | 179352 | 0.9 | 68.24 | [23 empty] | Single Speed DX AC | Electric | Cycling | SmallHotel PTAC Operation | SmallHotel PTAC OA Damper | [6 empty] | Electric | ConstantVolume | Cycling | 0.2 | Always On |  |  | 0.6045 | 1018.7736 | 0.95 |  |  |  | Hydraulic | 2
90.1-2004 | SmallOffice |  | ASHRAESmallOffice.osm | ASHRAE90120042007SmallOffice.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_Sched | [6 empty] | 1582.575 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.064 |  |  | 140 | 140 |  |  | 1951.7452 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | SmallOffice |  | ASHRAESmallOffice.osm | ASHRAE90120042007SmallOffice.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_Sched | [6 empty] | 1582.575 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.064 |  |  | 140 | 140 |  |  | 1951.7452 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | SmallOffice |  | ASHRAESmallOffice.osm | ASHRAE90120102013SmallOffice.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 861.3 | OfficeSmall Exterior_lighting_schedule_b | 50.7 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.064 |  |  | 140 | 140 |  |  | 1948.3331 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | SmallOffice |  | ASHRAE9012013SmallOffice.osm | ASHRAE90120102013SmallOffice.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 861.3 | OfficeSmall Exterior_lighting_schedule_b | 50.7 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.064 | 0.8 | 0 | 140 | 140 |  |  | 1948.3331 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | SmallOffice |  | ASHRAESmallOffice.osm | DOERefSmallOffice.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.05 |  |  | 140 | 140 |  |  | 68.24 | [21 empty] | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | SmallOffice |  | DOERefPre1980SmallOffice.osm | DOERefSmallOffice.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | CORE_ZN | 0.05 |  |  | 140 | 140 |  |  | 68.24 | [21 empty] | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_Sched | [6 empty] | 1634 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.064 |  |  | 140 | 140 |  |  | 1948.33 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2007 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_Sched | [6 empty] | 1634 | OfficeSmall Exterior_Lgt_ALWAYS_ON |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.064 |  |  | 140 | 140 |  |  | 1948.33 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2010 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.064 |  |  | 140 | 140 |  |  | 1948.33 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2013 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed Heat Pump | Single Speed Heat Pump | Cycling | Gas | OfficeSmall HVACOperationSchd | OfficeSmall MinOA_MotorizedDamper_Sched |  |  |  |  | 896.07 | OfficeSmall Exterior_lighting_schedule_b | 40.54 | OfficeSmall Exterior_lighting_schedule_a |  |  |  |  | 40 | Electricity | 40000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.064 | 0.8 | 0 | 140 | 140 |  |  | 1948.33 | [21 empty] | OfficeSmall HTGSETP_SCH_NO_OPTIMUM | OfficeSmall CLGSETP_SCH_NO_SETBACK | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref 1980-2004 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.05 |  |  | 140 | 140 |  |  | 68.24 | [21 empty] | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
DOE Ref Pre-1980 | SmallOfficeDetailed |  | ASHRAESmallOfficeDetailed.osm | ASHRAESmallOfficeDetailed.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | SmallOffice PSZ-AC Operation | SmallOffice PSZ-AC OA Damper | [6 empty] | 2766 | SmallOffice Exterior Lights Always On |  |  |  |  | 40 | Natural Gas | 2883000 | 140 | OfficeSmall BLDG_SWH_SCH | Mechanical | 0.05 |  |  | 140 | 140 |  |  | 68.24 | [21 empty] | Small Office HtgSetp | Small Office ClgSetp | [18 empty] | 0.6045 | 1018.7736 | 0.95 |  |  |  |  | 0
90.1-2004 | SuperMarket |  | ASHRAESuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched | [6 empty] | 15187 | Always On |  |  |  |  | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 |  |  | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
90.1-2007 | SuperMarket |  | ASHRAESuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched | [6 empty] | 15187 | Always On |  |  |  |  | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 |  |  | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
90.1-2010 | SuperMarket |  | ASHRAE9012010SuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched |  |  |  |  | 10125 | SuperMarket Exterior_lighting_schedule_b | [6 empty] | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 |  |  | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
90.1-2013 | SuperMarket |  | ASHRAE9012013SuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched |  |  |  |  | 10125 | SuperMarket Exterior_lighting_schedule_b | [6 empty] | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 | 0.8 | 0 | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
DOE Ref 1980-2004 | SuperMarket |  | ASHRAESuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched | [6 empty] | 15187 | Always On |  |  |  |  | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 |  |  | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
DOE Ref Pre-1980 | SuperMarket |  | ASHRAESuperMarket.osm | ASHRAESuperMarket.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume | Electric | SuperMarket HVACOperationSchd | SuperMarket MinOA_MotorizedDamper_Sched | [6 empty] | 15187 | Always On |  |  |  |  | 105 | Natural Gas | 2883259 | 140 | SuperMarket Bldg Swh |  | 0.1664 |  |  | 140 | 140 | 0.1 | 1 | 0 | [21 empty] | OfficeLarge HTGSETP_SCH_YES_OPTIMUM | OfficeLarge CLGSETP_SCH_NO_SETBACK
90.1-2004 | Warehouse |  | ASHRAEWarehouse.osm | ASHRAEWarehouse.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 7857.24 | Warehouse Exterior_Lgt_ALWAYS_ON |  |  |  |  | 20 | Electricity | 21000.8721 | 140 | Warehouse Office DHW Schedule | Zone1 Office | 0.12799 |  |  | 140 | 140 |  |  | 1648.0646 | [21 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
90.1-2007 | Warehouse |  | ASHRAEWarehouse.osm | ASHRAEWarehouse.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 7857.24 | Warehouse Exterior_Lgt_ALWAYS_ON |  |  |  |  | 20 | Electricity | 21000.8721 | 140 | Warehouse Office DHW Schedule | Zone1 Office | 0.12799 |  |  | 140 | 140 |  |  | 1648.0646 | [21 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
90.1-2010 | Warehouse |  | ASHRAE9012013Warehouse.osm | ASHRAEWarehouse.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched |  |  |  |  | 6197.4 | Warehouse Exterior_lighting_schedule_b | 113.8 | Warehouse Exterior_lighting_schedule_a |  |  |  |  | 20 | Electricity | 21000.8721 | 140 | Warehouse Office DHW Schedule | Zone1 Office | 0.12799 |  |  | 140 | 140 |  |  | 1641.2403 | [21 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
90.1-2013 | Warehouse |  | ASHRAE9012013Warehouse.osm | ASHRAEWarehouse.json | [5 empty] | Two Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched |  |  |  |  | 6197.4 | Warehouse Exterior_lighting_schedule_b | 113.8 | Warehouse Exterior_lighting_schedule_a |  |  |  |  | 20 | Electricity | 21000.8721 | 140 | Warehouse Office DHW Schedule | Zone1 Office | 0.12799 | 0 | 0 | 140 | 140 |  |  | 1641.2403 | [21 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
DOE Ref 1980-2004 | Warehouse |  | DOERefWarehouse.osm | DOERefWarehouse.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | [9 empty] | Zone1 Office | [29 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
DOE Ref Pre-1980 | Warehouse |  | DOERefWarehouse.osm | DOERefWarehouse.json | [5 empty] | Single Speed DX AC | Gas | ConstantVolume |  | Warehouse FanSched | Warehouse MinOA_MotorizedDamper_Sched | [6 empty] | 10958 | Warehouse Exterior_Lgt_ALWAYS_ON | [9 empty] | Zone1 Office | [29 empty] | Warehouse HtgSetp | Warehouse ClgSetp | [11 empty] | Gas | ConstantVolume | OnOff | 0.2 | Always On | [9 empty] | 0
90.1-2004 | Laboratory |  | ASHRAELaboratory.osm | ASHRAELaboratory.json | [23 empty] | 300 | Natural Gas | 300000 | 140 |  | Lab_bot_corridor_ZN |  |  |  | 140 | 131 | 29891 | 0.3 | 7197.67
90.1-2007 | Laboratory |  | ASHRAELaboratory.osm | ASHRAELaboratory.json | [23 empty] | 300 | Natural Gas | 300000 | 140 |  | Lab_bot_corridor_ZN |  |  |  | 140 | 131 | 29891 | 0.3 | 7197.67
90.1-2010 | Laboratory |  | ASHRAELaboratory.osm | ASHRAELaboratory.json | [23 empty] | 300 | Natural Gas | 300000 | 140 |  | Lab_bot_corridor_ZN |  |  |  | 140 | 131 | 29891 | 0.3 | 6835.99
90.1-2013 | Laboratory |  | ASHRAELaboratory.osm | ASHRAELaboratory.json | [23 empty] | 300 | Natural Gas | 300000 | 140 |  | Lab_bot_corridor_ZN |  |  |  | 140 | 131 | 29891 | 0.3 | 6835.99

## Climate Zones
A climate zone is a geographic area defined in a standards document
0 | 1 | 2 | 3
Name | Standard | Representative City | BCL Weather Component ID
ASHRAE 169-2006-0A | ASHRAE 169-2006 | Hanoi, Vietnam
ASHRAE 169-2006-0B | ASHRAE 169-2006 | Abu Dhabi, UAE
ASHRAE 169-2006-1A | ASHRAE 169-2006 | Miami, FL
ASHRAE 169-2006-1B | ASHRAE 169-2006 | Riyadh, Saudi Arabia
ASHRAE 169-2006-2A | ASHRAE 169-2006 | Houston, TX
ASHRAE 169-2006-2B | ASHRAE 169-2006 | Phoenix, AZ
ASHRAE 169-2006-3A | ASHRAE 169-2006 | Memphis, TN
ASHRAE 169-2006-3B | ASHRAE 169-2006 | El Paso, TX
ASHRAE 169-2006-3C | ASHRAE 169-2006 | San Francisco, CA
ASHRAE 169-2006-4A | ASHRAE 169-2006 | Baltimore, MD
ASHRAE 169-2006-4B | ASHRAE 169-2006 | Albuquerque, NW
ASHRAE 169-2006-4C | ASHRAE 169-2006 | Salem, OR
ASHRAE 169-2006-5A | ASHRAE 169-2006 | Chicago, IL
ASHRAE 169-2006-5B | ASHRAE 169-2006 | Boise, ID
ASHRAE 169-2006-5C | ASHRAE 169-2006 | Vancouver, BC
ASHRAE 169-2006-6A | ASHRAE 169-2006 | Burlington, VT
ASHRAE 169-2006-6B | ASHRAE 169-2006 | Helena, MT
ASHRAE 169-2006-7A | ASHRAE 169-2006 | Duluth, MN
ASHRAE 169-2006-7B | ASHRAE 169-2006 | Duluth, MN
ASHRAE 169-2006-8A | ASHRAE 169-2006 | Fairbanks, AK
ASHRAE 169-2006-8B | ASHRAE 169-2006 | Fairbanks, AK
ASHRAE 169-2013-0A | ASHRAE 169-2013 | Hanoi, Vietnam
ASHRAE 169-2013-0B | ASHRAE 169-2013 | Abu Dhabi, UAE
ASHRAE 169-2013-1A | ASHRAE 169-2013 | Honolulu, HI
ASHRAE 169-2013-1B | ASHRAE 169-2013 | New Delhi, India
ASHRAE 169-2013-2A | ASHRAE 169-2013 | Tampa, FL
ASHRAE 169-2013-2B | ASHRAE 169-2013 | Tucson, AZ
ASHRAE 169-2013-3A | ASHRAE 169-2013 | Atlanta, GA
ASHRAE 169-2013-3B | ASHRAE 169-2013 | El Paso, TX
ASHRAE 169-2013-3C | ASHRAE 169-2013 | San Diego, CA
ASHRAE 169-2013-4A | ASHRAE 169-2013 | New York, NY
ASHRAE 169-2013-4B | ASHRAE 169-2013 | Albuquerque, NW
ASHRAE 169-2013-4C | ASHRAE 169-2013 | Seattle, WA
ASHRAE 169-2013-5A | ASHRAE 169-2013 | Buffalo, NY
ASHRAE 169-2013-5B | ASHRAE 169-2013 | Denver, CO
ASHRAE 169-2013-5C | ASHRAE 169-2013 | Port Angeles, WA
ASHRAE 169-2013-6A | ASHRAE 169-2013 | Rochester, MN
ASHRAE 169-2013-6B | ASHRAE 169-2013 | Great Falls, MT
ASHRAE 169-2013-7A | ASHRAE 169-2013 | International Falls, MN
ASHRAE 169-2013-7B | ASHRAE 169-2013 | International Falls, MN
ASHRAE 169-2013-8A | ASHRAE 169-2013 | Fairbanks, AK
ASHRAE 169-2013-8B | ASHRAE 169-2013 | Fairbanks, AK

## Climate Zone Sets
A climate zone set is a group of climate zones
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39
Name | Climate Zone | Climate Zone2 | Climate Zone3 | Climate Zone4 | Climate Zone5 | Climate Zone6 | Climate Zone7 | Climate Zone8 | Climate Zone9 | Climate Zone10 | Climate Zone11 | Climate Zone12 | Climate Zone13 | Climate Zone14 | Climate Zone15 | Climate Zone16 | Climate Zone17 | Climate Zone18 | Climate Zone19 | Climate Zone20 | Climate Zone21 | Climate Zone22 | Climate Zone23 | Climate Zone24 | Climate Zone25 | Climate Zone26 | Climate Zone27 | Climate Zone28 | Climate Zone29 | Climate Zone30 | Climate Zone31 | Climate Zone32 | Climate Zone33 | Climate Zone34 | Climate Zone35 | Climate Zone36 | Climate Zone37 | Climate Zone38 | Climate Zone39
ClimateZone 0 | ASHRAE 169-2006-0A | ASHRAE 169-2006-0B | ASHRAE 169-2013-0A | ASHRAE 169-2013-0B
ClimateZone 0A | ASHRAE 169-2006-0A | ASHRAE 169-2013-0A
ClimateZone 0B | ASHRAE 169-2006-0B | ASHRAE 169-2013-0B
ClimateZone 1 | ASHRAE 169-2006-1A | ASHRAE 169-2006-1B | ASHRAE 169-2013-1A | ASHRAE 169-2013-1B
ClimateZone 1A | ASHRAE 169-2006-1A | ASHRAE 169-2013-1A
ClimateZone 1B | ASHRAE 169-2006-1B | ASHRAE 169-2013-1B
ClimateZone 2 | ASHRAE 169-2006-2A | ASHRAE 169-2006-2B | ASHRAE 169-2013-2A | ASHRAE 169-2013-2B
ClimateZone 2A | ASHRAE 169-2006-2A | ASHRAE 169-2013-2A
ClimateZone 2B | ASHRAE 169-2006-2B | ASHRAE 169-2013-2B
ClimateZone 3 | ASHRAE 169-2006-3A | ASHRAE 169-2006-3B | ASHRAE 169-2006-3C | ASHRAE 169-2013-3A | ASHRAE 169-2013-3B | ASHRAE 169-2013-3C
ClimateZone 3A | ASHRAE 169-2006-3A | ASHRAE 169-2013-3A
ClimateZone 3B | ASHRAE 169-2006-3B | ASHRAE 169-2013-3B
ClimateZone 3C | ASHRAE 169-2006-3C | ASHRAE 169-2013-3C
ClimateZone 4 | ASHRAE 169-2006-4A | ASHRAE 169-2006-4B | ASHRAE 169-2006-4C | ASHRAE 169-2013-4A | ASHRAE 169-2013-4B | ASHRAE 169-2013-4C
ClimateZone 4A | ASHRAE 169-2006-4A | ASHRAE 169-2013-4A
ClimateZone 4B | ASHRAE 169-2006-4B | ASHRAE 169-2013-4B
ClimateZone 4C | ASHRAE 169-2006-4C | ASHRAE 169-2013-4C
ClimateZone 5 | ASHRAE 169-2006-5A | ASHRAE 169-2006-5B | ASHRAE 169-2006-5C | ASHRAE 169-2013-5A | ASHRAE 169-2013-5B | ASHRAE 169-2013-5C
ClimateZone 5A | ASHRAE 169-2006-5A | ASHRAE 169-2013-5A
ClimateZone 5B | ASHRAE 169-2006-5B | ASHRAE 169-2013-5B
ClimateZone 5C | ASHRAE 169-2006-5C | ASHRAE 169-2013-5C
ClimateZone 6 | ASHRAE 169-2006-6A | ASHRAE 169-2006-6B | ASHRAE 169-2013-6A | ASHRAE 169-2013-6B
ClimateZone 6A | ASHRAE 169-2006-6A | ASHRAE 169-2013-6A
ClimateZone 6B | ASHRAE 169-2006-6B | ASHRAE 169-2013-6B
ClimateZone 7 | ASHRAE 169-2006-7A | ASHRAE 169-2006-7B | ASHRAE 169-2013-7A | ASHRAE 169-2013-7B
ClimateZone 8 | ASHRAE 169-2006-8A | ASHRAE 169-2006-8B | ASHRAE 169-2013-8A | ASHRAE 169-2013-8B

## Parking
Assumptions for parking area required for different building types
Building Type | Building Area Per Spot | Units Per Spot | Students Per Spot | Beds Per Spot | Parking Area Per Spot (ft^2) | Notes
SmallOffice | 250 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MediumOffice | 250 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
LargeOffice | 620 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Retail | 285.7 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
StripMall | 215 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
PrimarySchool |  |  | 17 |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
SecondarySchool |  |  | 8 |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Outpatient | 200 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Hospital |  |  |  | 0.83 | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
SmallHotel |  | 1 |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
LargeHotel |  | 1 |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Warehouse | 1000 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
QuickServiceRestaurant | 100 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
FullServiceRestaurant | 100 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MidriseApartment |  | 0.45 |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
HighriseApartment |  | 0.45 |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
SuperMarket | 285.7 |  |  |  | 405 | From NREL Reference Building (45002 ft^2 building/63810 ft^2 parking area at 405 per spot 157 spots)
Parking surface |  |  |  |  | 405
Parking garage |  |  |  |  | 486
SmallDataCenterLowITE | 0
SmallDataCenterHighITE | 0
LargeDataCenterLowITE | 0
LargeDataCenterHighITE | 0
SmallOfficeDetailed | 250 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MediumOfficeDetailed | 250 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
LargeOfficeDetailed | 620 |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Courthouse |  |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
College |  |  |  |  | 405 | Based on Table 4.17 Illuminated Parking Area from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010

## Entryways
Assumptions about entryways and facades, used for exterior lighting allowances
Building Type | Rollup Doors per 10,000 (ft^2) | Entrance Doors per 10,000 (ft^2) | Others Doors per 10,000 (ft^2) | Entrance Canopies | Emergency Canopies | Canopy Size (ft^2) | Floor Area per Drive Through Window (ft^2) | Notes
SmallOffice | 0.47 | 2 | 2 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MediumOffice | 0.13 | 1 | 3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
LargeOffice | 0 | 1 | 3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Retail | 1.84 | 1 | 2.93 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
StripMall | 0.05 | 6 | 6.6 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
PrimarySchool | 0.07 | 2 | 3.3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
SecondarySchool | 0.1 | 2 | 2.45 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Outpatient | 0.1 | 1 | 5.19 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
Hospital | 0.03 | 2 | 3.8 |  | 1 | 720 |  | No source for canopy size, Table 5.41. Exterior Lighting Savings Summary for Addendum 90.1-07i doesn't indicate canopy lighting. Section 5.4.2 Exterior Lights in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock shows their use.
SmallHotel | 0 | 2 | 28.91 | 1 |  | 720 |  | SmallHotel appears to have exterior entries for all units, No source for canopy size, Table 5.41. Exterior Lighting Savings Summary for Addendum 90.1-07i doesn't indicate canopy lighting. Section 5.4.2 Exterior Lights in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock shows their use.
LargeHotel | 0 | 2 | 2.27 | 1 |  | 1620 |  | No source for canopy size, Table 5.41. Exterior Lighting Savings Summary for Addendum 90.1-07i doesn't indicate canopy lighting. Section 5.4.2 Exterior Lights in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock shows their use.
Warehouse | 3.67 | 1 | 2 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
QuickServiceRestaurant | 0 | 2 | 1 |  |  |  | 2500 | No source for drive through count, Table 5.41. Exterior Lighting Savings Summary for Addendum 90.1-07i doesn't indicate drive through lighting. Section 5.4.2 Exterior Lights in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock shows their use.
FullServiceRestaurant | 0 | 1 | 3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MidriseApartment | 0 | 1 | 1.13 |  |  |  |  | Midrise not in table 4.18, using half of values from LargeHotel.
HighriseApartment | 0 | 1 | 1.13 |  |  |  |  | Highrise not in table 4.18, using half of values from LargeHotel.
SuperMarket | 1.84 | 1 | 2.93 |  |  |  |  | SuperMarket not in table 4.18, using values from RetailStandAlone. Consistant with SuperMarket parking area used in U.S. Department of Energy Commercial Reference Building Models of the National Building Stock report.
Courthouse
SmallDataCenterLowITE
SmallDataCenterHighITE
LargeDataCenterLowITE
LargeDataCenterHighITE
SmallOfficeDetailed | 0.47 | 2 | 2 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
MediumOfficeDetailed | 0.13 | 1 | 3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
LargeOfficeDetailed | 0 | 1 | 3 |  |  |  |  | Based on Table 4.18 Number of Doors by Door Type from Achieving the 30% Goal: Energy and Cost Savings Analysis of ASHRAE Standard 90.1-2010
College

## DEER Lighting Fractions
DEER Radiant Fraction Table
| LtToSpc Linear Fluorescent | LtToSpc Compact Fluorescent | LtToSpc High Bay | LtToSpc Speciality Lighting | LtToSpc Exit Lighting | Return Air Fraction Linear Fluorescent | Return Air Fraction Compact Fluorescent | Return Air Fraction Linear Fluorescent | Return Air Fraction Linear Fluorescent | Return Air Fraction Linear Fluorescent | Radiant Fraction Linear Fluorescent | Radiant Fraction Compact Fluorescent | Radiant Fraction High Bay | Radiant Fraction Speciality Lighting | Radiant Fraction Exit Lighting | OthRadFrac Linear Fluorescent | OthRadFrac Compact Fluorescent | OthRadFrac High Bay | OthRadFrac Speciality Lighting | OthRadFrac Exit Lighting
Plenum | 0.94 | 0.82 | 0.82 | 0.8 | 1 | 0.06 | 0.18 | 0.18 | 0.2 | 0 | 0.55 | 0.66 | 0.66 | 0.71 | 0.71 | 0.09 | 0.09 | 0.09 | 0.09 | 0
No Plenum | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0.63 | 0.7 | 0.7 | 0.71 | 0.71 | 0 | 0 | 0 | 0 | 0

## Materials
Each Material represents a layer of typical building material. Materials are referenced on the Constructions tab.
|  | Opaque Material Properties | [9 empty] | Simple Glazing Material Properties |  |  | Detailed Glazing Material Properties | [12 empty] | Standards Information
Name | Material Type | Roughness | Thickness (in) | Conductivity (Btu*in/hr*ft^2*F) | Resistance (hr*ft^2*F/Btu) | Density (lb/ft^3) | Specific Heat (Btu/lbm*F) | Thermal Absorptance | Solar Absorptance | Visible Absorptance | Gas Type | U-Factor (Btu/hr*ft^2*F) | Solar Heat Gain Coefficient | Visible Transmittance | Optical Data Type | Solar Transmittance At Normal Incidence | Front Side Solar Reflectance At Normal Incidence | Back Side Solar Reflectance At Normal Incidence | Visible Transmittance At Normal Incidence | Front Side Visible Reflectance At Normal Incidence | Back Side Visible Reflectance At Normal Incidence | Infrared Transmittance At Normal Incidence | Front Side Infrared Hemispherical Emissivity | Back Side Infrared Hemispherical Emissivity | Dirt Correction Factor For Solar And Visible Transmittance | Solar Diffusing | Frame width (in) | Material Standard | Material Standard Source | Code Category | Code Identifier | Framing Material | Framing Configuration | Framing Depth | Framing Size | Cavity Insulation (hr*ft^2*F/Btu) | Notes
1 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.38 | 5.0004 | 0.075994 | 115.81 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Masonry Materials | 1 Coat Stucco | [5 empty] | From CEC Title24 2013
1/2 in. Gypsum Board | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.45071 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.5
1/2IN Gypsum | StandardOpaqueMaterial | Smooth | 0.5 | 1.1094 | 0.45071 | 48.9997 | 0.19824 | 0.9 | 0.4 | 0.4
10 PSF Roof - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 12.0048 | 0.0833 | 120 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 10 PSF Roof - 1 in. | [5 empty] | From CEC Title24 2013
100mm Normalweight concrete floor | StandardOpaqueMaterial | MediumRough | 4 | 16.0194 | 0.2497 | 144.9578 | 0.19885
12 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 12 | 16.0163 | 0.74924 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
15 PSF Roof - 1 1/2 in. | StandardOpaqueMaterial | VeryRough | 1.5 | 18.0072 | 0.0833 | 120 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 15 PSF Roof - 1 1/2 in. | [5 empty] | From CEC Title24 2013
1IN Stucco | StandardOpaqueMaterial | Smooth | 0.99606 | 4.7966 | 0.20766 | 115.9912 | 0.19991 | 0.9 | 0.7 | 0.92
25 PSF Roof - 2 1/2 in. | StandardOpaqueMaterial | VeryRough | 2.5 | 30.012 | 0.0833 | 120 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 25 PSF Roof - 2 1/2 in. | [5 empty] | From CEC Title24 2013
25mm Stucco | StandardOpaqueMaterial | Smooth | 1 | 4.9921 | 0.20032 | 115.8663 | 0.20063 | 0.9 | 0.7 | 0.7
3 Coat Stucco | StandardOpaqueMaterial | MediumRough | 0.88 | 4.3752 | 0.20113 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | 3 Coat Stucco | [5 empty] | From CEC Title24 2013
4 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.24975 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
4 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 4 | 16.0163 | 0.24975 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
5 PSF Roof - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 6.0024 | 0.0833 | 120 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | 5 PSF Roof - 1/2 in. | [5 empty] | From CEC Title24 2013
5/8 in. Gypsum Board | StandardOpaqueMaterial | MediumSmooth | 0.62598 | 1.1094 | 0.56428 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7
5/8 in. Plywood | StandardOpaqueMaterial | Smooth | 0.62598 | 0.83202 | 0.75237 | 33.9608 | 0.289 | 0.9 | 0.7 | 0.7
6 in. Heavyweight Concrete Roof | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.37462 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
6 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 6 | 16.0163 | 0.37462 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
8 in. Concrete Block Basement Wall | StandardOpaqueMaterial | MediumRough | 8 | 9.1938 | 0.87015 | 114.9923 | 0.21783 | 0.9 | 0.7 | 0.7
8 in. Concrete Block Wall | StandardOpaqueMaterial | MediumRough | 8 | 4.9921 | 1.6025 | 49.9424 | 0.19872 | 0.9 | 0.7 | 0.7
8 in. Normalweight Concrete Floor | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.49949 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
8 in. Normalweight Concrete Wall | StandardOpaqueMaterial | MediumRough | 8 | 16.0163 | 0.49949 | 144.9577 | 0.19872 | 0.9 | 0.7 | 0.7
8IN Concrete HW | StandardOpaqueMaterial | MediumRough | 8.0039 | 11.9921 | 0.66743 | 140.0259 | 0.19991 | 0.9 | 0.65 | 0.65
8IN CONCRETE HW RefBldg | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.7 | 0.7
Acoustic Ceiling | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.39521 | 1.2652 | 17.9793 | 0.31981 | 0.9 | 0.7 | 0.2
Acoustic Tile - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.3996 | 1.2513 | 18 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 1/2 in. | [5 empty] | From CEC Title24 2013
Acoustic Tile - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.3996 | 1.8769 | 18 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/4 in. | [5 empty] | From CEC Title24 2013
Acoustic Tile - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.39 | 0.97436 | 18 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Acoustic Tile - 3/8 in. | [5 empty] | From CEC Title24 2013
Adiabatic Material | MasslessOpaqueMaterial |  |  |  | 9999
Aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.56 | 0.32051 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Aggregate - 45 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.5996 | 0.39385 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - 5/8 in. | [5 empty] | From CEC Title24 2013
Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.5996 | 0.46887 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - 45 lb/ft3 - on metal lath - 3/4 in. | [5 empty] | From CEC Title24 2013
Aggregate - Perlite - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.38473 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 1/2 in. | [5 empty] | From CEC Title24 2013
Aggregate - Perlite - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 1.5 | 0.42 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - 5/8 in. | [5 empty] | From CEC Title24 2013
Aggregate - Perlite - on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.7004 | 0.44107 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Aggregate - Perlite - on metal lath - 3/4 in. | [5 empty] | From CEC Title24 2013
Air - Cavity - Wall Roof Ceiling - 4 in. or more | StandardOpaqueMaterial | Smooth | 6 | 6.5196 | 0.9203 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | JA4 | Air | Air - Cavity - Wall Roof Ceiling - 4 in. or more | [5 empty] | From CEC Title24 2013
Air - Ceiling - 1 1/2 in. | StandardOpaqueMaterial | Smooth | 1.5 | 1.95 | 0.76923 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Ceiling - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6804 | 0.73486 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Ceiling - 3 1/2 in. | StandardOpaqueMaterial | Smooth | 3.5 | 4.38 | 0.79909 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Ceiling - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.9996 | 0.7503 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Ceiling - 3/4 in. | [5 empty] | From CEC Title24 2013
Air - Floor - 1 1/2 in. | StandardOpaqueMaterial | Smooth | 1.5 | 1.5996 | 0.93773 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Floor - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6504 | 0.76876 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Floor - 3 1/2 in. | StandardOpaqueMaterial | Smooth | 3.5 | 3.5004 | 0.99989 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Floor - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.8796 | 0.85266 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Floor - 3/4 in. | [5 empty] | From CEC Title24 2013
Air - Metal Wall Framing - 16 or 24 in. OC | StandardOpaqueMaterial | Smooth | 5.5 | 8.46 | 0.65012 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | JA4 | Air | Air - Metal Wall Framing - 16 or 24 in. OC | [5 empty] | From CEC Title24 2013
Air - Roof - 1 1/2 in. | StandardOpaqueMaterial | Smooth | 1.5 | 1.8804 | 0.7977 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Roof - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.66 | 0.75758 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Roof - 3 1/2 in. | StandardOpaqueMaterial | Smooth | 3.5 | 4.2696 | 0.81975 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Roof - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.93 | 0.80645 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Roof - 3/4 in. | [5 empty] | From CEC Title24 2013
Air - Wall - 1 1/2 in. | StandardOpaqueMaterial | Smooth | 1.5 | 1.7196 | 0.8723 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Wall - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6504 | 0.76876 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Wall - 3 1/2 in. | StandardOpaqueMaterial | Smooth | 3.5 | 4.1196 | 0.8496 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Air - Wall - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.8904 | 0.84232 | 0.08 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Doug | Air | Air - Wall - 3/4 in. | [5 empty] | From CEC Title24 2013
AIR 13MM | Gas |  | 0.5 | [7 empty] | Air
AIR 3MM | Gas |  | 0.12598 | [7 empty] | Air
AIR 6MM | Gas |  | 0.24803 | [7 empty] | Air
Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.5222 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.9898 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.1389 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.2644 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.2948 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.3612 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5304 | 3.4502 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.8082 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Double glass with no low e - R7 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.9244 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8496 | 3.8489 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.1004 | 4.0622 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.35 | 4.2 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.6104 | 4.266 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.86 | 4.3387 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.5604 | 3.2655 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6996 | 3.6449 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.9103 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.8196 | 3.9898 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 1.08 | 4.1389 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.3296 | 4.2644 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.5996 | 4.2948 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.8504 | 4.3612 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.51 | 3.5882 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.6696 | 3.8082 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/ Thrml Break - Triple or low e glass - R7 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.8304 | 2.7336 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.6504 | 5.0277 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8304 | 5.3829 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0046 | 5.6438 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.7712 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.8888 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4404 | 4.1553 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.54 | 4.7222 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Double glass with no low e coatings - R7 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1304 | 2.0081 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.66 | 4.9545 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.84 | 5.3214 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 1.0104 | 5.6116 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1904 | 5.7712 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.38 | 5.8478 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.4704 | 3.8903 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5604 | 4.5503 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.69 | 3.2899 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - No Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.63648 | 5.1376 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R10 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.8196 | 5.4539 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R15 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.9996 | 5.6723 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R20 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 1.1796 | 5.824 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R25 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.3704 | 5.8888 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R30 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.41724 | 4.386 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R4 Ins. | [5 empty] | From CEC Title24 2013
Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.5304 | 4.8077 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Aluminum w/out Thrml Break - Triple or low e glass - R7 Ins. | [5 empty] | From CEC Title24 2013
ARGON 13MM | Gas |  | 0.5 | [7 empty] | Argon
Asbestos or cement shingles - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.7904 | 0.21224 | 120 | 0.24 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Asbestos or cement shingles - 3/8 in. | [5 empty] | From CEC Title24 2013
Ash - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1004 | 0.90876 | 40.06 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Ash - 1 in. | [5 empty] | From CEC Title24 2013
Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 3 | 0.25 | 100 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 100 lb/ft3 - 3/4 in. | [5 empty] | From CEC Title24 2013
Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 8.0004 | 0.093745 | 144 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt - bitumen with inert fill - 144 lb/ft3 - 3/4 in. | [5 empty] | From CEC Title24 2013
Asphalt roll roofing - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.14966 | 70 | 0.36 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Asphalt roll roofing - 1/4 in. | [5 empty] | From CEC Title24 2013
Asphalt Shingles | StandardOpaqueMaterial | VeryRough | 0.12598 | 0.27734 | 0.45426 | 69.9193 | 0.30095 | 0.9 | 0.7 | 0.7
Asphalt shingles - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 0.5604 | 0.44611 | 69.89 | 0.3 | [20 empty] | CEC Title24-2013 | CEC Doug | Roofing | Asphalt shingles - 1/4 in. | [5 empty] | From CEC Title24 2013
AtticFloor Insulation | StandardOpaqueMaterial | MediumRough | 9.3661 | 0.33974 | 27.5685 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Birch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1904 | 0.84005 | 43.93 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Birch - 1 in. | [5 empty] | From CEC Title24 2013
BLUE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.48 | 0.05 | 0.05 | 0.57 | 0.06 | 0.06 | 0 | 0.84 | 0.84 | 1 | FALSE
Brick - 48 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | Rough | 3.63 | 1.5 | 2.42 | 48 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - 48 lb/ft3 - 3 5/8 in. | [5 empty] | From CEC Title24 2013
Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | StandardOpaqueMaterial | MediumRough | 3.63 | 8.22 | 0.44161 | 139.78 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Brick - fired clay - 140 lb/ft3 - 3 5/8 in. | [5 empty] | From CEC Title24 2013
BRONZE 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.482 | 0.054 | 0.054 | 0.534 | 0.057 | 0.057 | 0 | 0.84 | 0.84 | 1 | FALSE
Building Paper - 1/16 in. | StandardOpaqueMaterial | MediumSmooth | 0.06 | 2.0004 | 0.029994 | 70 | 0.3 | [20 empty] | CEC Title24-2013 | CEC Doug | Building Membrane | Building Paper - 1/16 in. | [5 empty] | From CEC Title24 2013
Built-up Roofing | StandardOpaqueMaterial | Rough | 0.37402 | 1.1094 | 0.33715 | 69.9193 | 0.34872 | 0.9 | 0.7 | 0.7
Built-up roofing - 3/8 in. | StandardOpaqueMaterial | VeryRough | 0.38 | 1.14 | 0.33333 | 70 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Built-up roofing - 3/8 in. | [5 empty] | From CEC Title24 2013
Built-up Roofing - Highly Reflective | StandardOpaqueMaterial | Rough | 0.37402 | 1.1094 | 0.33715 | 69.9193 | 0.34872 | 0.75 | 0.45 | 0.7
Bulk Storage Products Material | StandardOpaqueMaterial | Rough | 96.0002 | 9.9981 | 9.6019 | 12.5 | 0.19987 | 0.9 | 0.7 | 0.7
California Redwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.78 | 1.2821 | 26.21 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | California Redwood - 1 in. | [5 empty] | From CEC Title24 2013
Carpet - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.3156 | 2.3764 | 18 | 0.33 | [20 empty] | CEC Title24-2013 | CEC Doug | Finish Materials | Carpet - 3/4 in. | [5 empty] | From CEC Title24 2013
Carpet - 3/4 in. CBES | StandardOpaqueMaterial | Smooth | 0.75 | 0.34691 |  | 18 | 0.33 | 0.9 | 0.7 | 0.8
ceiling_2_Insulation | StandardOpaqueMaterial | Smooth | 3.9677 | 0.15963 |  | 1 | 0.27 | 0.9 | 0.7 | 0.8
Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.1704 | 8.8028 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 1/2 in. R8.8 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | StandardOpaqueMaterial | Rough | 1 | 0.1704 | 5.8685 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1 in. R5.9 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | StandardOpaqueMaterial | Rough | 0.5 | 0.1704 | 2.9343 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/2 in. R2.9 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | StandardOpaqueMaterial | Rough | 0.25 | 0.1704 | 1.4671 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/4 in. R1.5 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | StandardOpaqueMaterial | Rough | 0.13 | 0.1704 | 0.76291 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 1/8 in. R0.7 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | StandardOpaqueMaterial | Rough | 2.5 | 0.1704 | 14.6714 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 1/2 in. R15 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 2 in. R12 | StandardOpaqueMaterial | Rough | 2 | 0.1704 | 11.7371 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 2 in. R12 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | StandardOpaqueMaterial | Rough | 3.5 | 0.1704 | 20.5399 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 1/2 in. R21 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 3 in. R18 | StandardOpaqueMaterial | Rough | 3 | 0.1704 | 17.6056 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 3 in. R18 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | StandardOpaqueMaterial | Rough | 4.5 | 0.1704 | 26.4085 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 1/2 in. R26 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 4 in. R23 | StandardOpaqueMaterial | Rough | 4 | 0.1704 | 23.4742 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 4 in. R23 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | StandardOpaqueMaterial | Rough | 5.5 | 0.1704 | 32.277 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 1/2 in. R32 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 5 in. R29 | StandardOpaqueMaterial | Rough | 5 | 0.1704 | 29.3427 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 5 in. R29 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | StandardOpaqueMaterial | Rough | 6.5 | 0.1704 | 38.1455 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 1/2 in. R38 | [5 empty] | From CEC Title24 2013
Cellular polyisocyanurate (unfaced) - 6 in. R35 | StandardOpaqueMaterial | Rough | 6 | 0.1704 | 35.2113 | 1.5 | 0.38 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Cellular polyisocyanurate (unfaced) - 6 in. R35 | [5 empty] | From CEC Title24 2013
Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.9231 | 130 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.7596 | 2.1279 | 130 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Clay - Part Grouted and Empty - 130 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.7 | 2.2222 | 130 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.12 | 2.5641 | 130 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Clay - Part Grouted and Insulated - 130 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Clay - Solid Grout - 130 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9 | 1.5385 | 130 | 0.17 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Clay - Solid Grout - 130 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.56 | 1.7544 | 130 | 0.17 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Clay - Solid Grout - 130 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Clay tile - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.1896 | 2.6371 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Clay tile - 1/2 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 1 cell deep - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 3.75 | 0.8 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 3 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 1 cell deep - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6 | 1.1111 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 1 cell deep - 4 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 2 cells deep - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5 | 2.2222 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 10 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 2 cells deep - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.9504 | 1.5188 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 6 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 2 cells deep - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.32 | 1.8519 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 2 cells deep - 8 in. | [5 empty] | From CEC Title24 2013
Clay tile - hollow - 3 cells deep - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.8 | 2.5 | 85 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Clay tile - hollow - 3 cells deep - 12 in. | [5 empty] | From CEC Title24 2013
Clay Tile - Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 12.504 | 0.03039 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Clay Tile - Paver | [5 empty] | From CEC Title24 2013
CLEAR 2.5MM | StandardGlazing |  | 0.098425 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.8 | 0.075 | 0.075 | 0.901 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
Clear 3mm | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.837 | 0.075 | 0.075 | 0.898 | 0.081 | 0.081 | 0 | 0.84 | 0.84 | 1 | FALSE
CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.775 | 0.071 | 0.071 | 0.881 | 0.08 | 0.08 | 0 | 0.84 | 0.84 | 1 | FALSE
COATED POLY-55 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.32 | 0.582 | 0.593 | 0.551 | 0.336 | 0.375 | 0 | 0.046 | 0.72 | 1 | FALSE
COATED POLY-77 | StandardGlazing |  | 0.020079 | 0.97069 | 1.0302 | [9 empty] | SpectralAverage | 0.504 | 0.402 | 0.398 | 0.766 | 0.147 | 0.167 | 0 | 0.075 | 0.72 | 1 | FALSE
Compliance Insulation R0.01 | StandardOpaqueMaterial | MediumSmooth | 0.0016 | 0.1596 | 0.010025 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.01 | [5 empty] | From CEC Title24 2013
Compliance Insulation R0.02 | StandardOpaqueMaterial | MediumSmooth | 0.0032 | 0.1596 | 0.02005 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.02 | [5 empty] | From CEC Title24 2013
Compliance Insulation R0.10 | StandardOpaqueMaterial | MediumSmooth | 0.016 | 0.1596 | 0.10025 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R0.10 | [5 empty] | From CEC Title24 2013
Compliance Insulation R1.35 | StandardOpaqueMaterial | MediumSmooth | 0.216 | 0.1596 | 1.3534 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.35 | [5 empty] | From CEC Title24 2013
Compliance Insulation R1.41 | StandardOpaqueMaterial | MediumSmooth | 0.2256 | 0.1596 | 1.4135 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.41 | [5 empty] | From CEC Title24 2013
Compliance Insulation R1.54 | StandardOpaqueMaterial | MediumSmooth | 0.2464 | 0.1596 | 1.5439 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R1.54 | [5 empty] | From CEC Title24 2013
Compliance Insulation R10.06 | StandardOpaqueMaterial | MediumSmooth | 1.6096 | 0.1596 | 10.0852 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R10.06 | [5 empty] | From CEC Title24 2013
Compliance Insulation R12.55 | StandardOpaqueMaterial | MediumSmooth | 2.008 | 0.1596 | 12.5815 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.55 | [5 empty] | From CEC Title24 2013
Compliance Insulation R12.69 | StandardOpaqueMaterial | MediumSmooth | 2.0304 | 0.1596 | 12.7218 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R12.69 | [5 empty] | From CEC Title24 2013
Compliance Insulation R13.99 | StandardOpaqueMaterial | MediumSmooth | 2.2384 | 0.1596 | 14.0251 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R13.99 | [5 empty] | From CEC Title24 2013
Compliance Insulation R14.14 | StandardOpaqueMaterial | MediumSmooth | 2.2624 | 0.1596 | 14.1754 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.14 | [5 empty] | From CEC Title24 2013
Compliance Insulation R14.32 | StandardOpaqueMaterial | MediumSmooth | 2.2912 | 0.1596 | 14.3559 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.32 | [5 empty] | From CEC Title24 2013
Compliance Insulation R14.60 | StandardOpaqueMaterial | MediumSmooth | 2.336 | 0.1596 | 14.6366 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R14.60 | [5 empty] | From CEC Title24 2013
Compliance Insulation R15.54 | StandardOpaqueMaterial | MediumSmooth | 2.4864 | 0.1596 | 15.5789 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R15.54 | [5 empty] | From CEC Title24 2013
Compliance Insulation R16.58 | StandardOpaqueMaterial | MediumSmooth | 2.6528 | 0.1596 | 16.6216 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.58 | [5 empty] | From CEC Title24 2013
Compliance Insulation R16.69 | StandardOpaqueMaterial | MediumSmooth | 2.6704 | 0.1596 | 16.7318 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R16.69 | [5 empty] | From CEC Title24 2013
Compliance Insulation R17.67 | StandardOpaqueMaterial | MediumSmooth | 2.8272 | 0.1596 | 17.7143 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R17.67 | [5 empty] | From CEC Title24 2013
Compliance Insulation R19.63 | StandardOpaqueMaterial | MediumSmooth | 3.1408 | 0.1596 | 19.6792 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R19.63 | [5 empty] | From CEC Title24 2013
Compliance Insulation R2.15 | StandardOpaqueMaterial | MediumSmooth | 0.344 | 0.1596 | 2.1554 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.15 | [5 empty] | From CEC Title24 2013
Compliance Insulation R2.19 | StandardOpaqueMaterial | MediumSmooth | 0.3504 | 0.1596 | 2.1955 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.19 | [5 empty] | From CEC Title24 2013
Compliance Insulation R2.85 | StandardOpaqueMaterial | MediumSmooth | 0.456 | 0.1596 | 2.8571 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.85 | [5 empty] | From CEC Title24 2013
Compliance Insulation R2.89 | StandardOpaqueMaterial | MediumSmooth | 0.4624 | 0.1596 | 2.8972 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R2.89 | [5 empty] | From CEC Title24 2013
Compliance Insulation R20.05 | StandardOpaqueMaterial | MediumSmooth | 3.208 | 0.1596 | 20.1003 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R20.05 | [5 empty] | From CEC Title24 2013
Compliance Insulation R21.18 | StandardOpaqueMaterial | MediumSmooth | 3.3888 | 0.1596 | 21.2331 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.18 | [5 empty] | From CEC Title24 2013
Compliance Insulation R21.39 | StandardOpaqueMaterial | MediumSmooth | 3.4224 | 0.1596 | 21.4436 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R21.39 | [5 empty] | From CEC Title24 2013
Compliance Insulation R22.48 | StandardOpaqueMaterial | MediumSmooth | 3.5968 | 0.1596 | 22.5363 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R22.48 | [5 empty] | From CEC Title24 2013
Compliance Insulation R24.86 | StandardOpaqueMaterial | MediumSmooth | 3.9776 | 0.1596 | 24.9223 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R24.86 | [5 empty] | From CEC Title24 2013
Compliance Insulation R25.16 | StandardOpaqueMaterial | MediumSmooth | 4.0256 | 0.1596 | 25.2231 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R25.16 | [5 empty] | From CEC Title24 2013
Compliance Insulation R28.63 | StandardOpaqueMaterial | MediumSmooth | 4.5808 | 0.1596 | 28.7018 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R28.63 | [5 empty] | From CEC Title24 2013
Compliance Insulation R3.63 | StandardOpaqueMaterial | MediumSmooth | 0.5808 | 0.1596 | 3.6391 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.63 | [5 empty] | From CEC Title24 2013
Compliance Insulation R3.70 | StandardOpaqueMaterial | MediumSmooth | 0.592 | 0.1596 | 3.7093 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R3.70 | [5 empty] | From CEC Title24 2013
Compliance Insulation R34.93 | StandardOpaqueMaterial | MediumSmooth | 5.5888 | 0.1596 | 35.0175 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R34.93 | [5 empty] | From CEC Title24 2013
Compliance Insulation R6.32 | StandardOpaqueMaterial | MediumSmooth | 1.0112 | 0.1596 | 6.3358 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.32 | [5 empty] | From CEC Title24 2013
Compliance Insulation R6.46 | StandardOpaqueMaterial | MediumSmooth | 1.0336 | 0.1596 | 6.4762 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R6.46 | [5 empty] | From CEC Title24 2013
Compliance Insulation R7.10 | StandardOpaqueMaterial | MediumSmooth | 1.136 | 0.1596 | 7.1178 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.10 | [5 empty] | From CEC Title24 2013
Compliance Insulation R7.18 | StandardOpaqueMaterial | MediumSmooth | 1.1488 | 0.1596 | 7.198 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.18 | [5 empty] | From CEC Title24 2013
Compliance Insulation R7.39 | StandardOpaqueMaterial | MediumSmooth | 1.1824 | 0.1596 | 7.4085 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R7.39 | [5 empty] | From CEC Title24 2013
Compliance Insulation R8.00 | StandardOpaqueMaterial | MediumSmooth | 1.28 | 0.1596 | 8.0201 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.00 | [5 empty] | From CEC Title24 2013
Compliance Insulation R8.07 | StandardOpaqueMaterial | MediumSmooth | 1.2912 | 0.1596 | 8.0902 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R8.07 | [5 empty] | From CEC Title24 2013
Compliance Insulation R9.83 | StandardOpaqueMaterial | MediumSmooth | 1.5697 | 0.1596 | 9.8352 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.83 | [5 empty] | From CEC Title24 2013
Compliance Insulation R9.94 | StandardOpaqueMaterial | MediumSmooth | 1.5904 | 0.1596 | 9.9649 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Compliance Insulation R9.94 | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 6.2496 | 1.6001 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 6.2496 | 1.9201 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 6.2496 | 0.32002 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 2 in. | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 6.2496 | 0.64004 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 6.2496 | 0.96006 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - 100 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 6.2496 | 1.2801 | 100 | 0.21 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 100 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 13.53 | 0.7391 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 13.53 | 0.88692 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 13.53 | 0.14782 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 2 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 13.53 | 0.29564 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 13.53 | 0.44346 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - 140 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 13.53 | 0.59128 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 140 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6804 | 2.7171 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6804 | 3.2605 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 2 in. | StandardOpaqueMaterial | MediumRough | 2 | 3.6804 | 0.54342 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 2 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 3.6804 | 1.0868 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.6804 | 1.6303 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - 80 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.6804 | 2.1737 | 79.87 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Concrete | Concrete - 80 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.5996 | 2.1741 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.16 | 2.3256 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.24 | 1.8519 | 105 | 0.15 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.9996 | 2.0002 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 105 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.8996 | 2.041 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.52 | 2.1739 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.48 | 1.7241 | 115 | 0.15 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.2396 | 1.887 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 115 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 5.1996 | 1.9232 | 125 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 5.88 | 2.0408 | 125 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.66 | 1.6393 | 125 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 4.4796 | 1.7859 | 125 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Hollow | Concrete - Part Grouted and Empty - 125 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.3996 | 2.9415 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.6 | 3.3333 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.64 | 2.2727 | 105 | 0.15 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 2.9604 | 2.7023 | 105 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 105 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 3.6996 | 2.703 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 3.96 | 3.0303 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 2.88 | 2.0833 | 115 | 0.15 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.2796 | 2.4393 | 115 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 115 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 4.1004 | 2.4388 | 125 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 4.32 | 2.7778 | 125 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 3.12 | 1.9231 | 125 | 0.14 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 3.5196 | 2.273 | 125 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units with Fill | Concrete - Part Grouted and Insulated - 125 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 105 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 8.4744 | 1.18 | 105 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 105 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 8.5704 | 1.4002 | 105 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 105 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 8.3328 | 0.72005 | 105 | 0.21 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 105 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 8.3328 | 0.96006 | 105 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 105 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 115 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 9.174 | 1.09 | 115 | 0.21 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 115 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 9.2304 | 1.3001 | 115 | 0.21 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 115 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.58997 | 115 | 0.2 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 115 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 9.1224 | 0.87696 | 115 | 0.2 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 115 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 125 lb/ft3 - 10 in. | StandardOpaqueMaterial | MediumRough | 10 | 10.1016 | 0.98994 | 125 | 0.2 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 10 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 125 lb/ft3 - 12 in. | StandardOpaqueMaterial | MediumRough | 12 | 10.0836 | 1.1901 | 125 | 0.2 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 12 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 125 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 10.17 | 0.58997 | 125 | 0.19 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Concrete - Solid Grout - 125 lb/ft3 - 8 in. | StandardOpaqueMaterial | MediumRough | 8 | 10.1268 | 0.78998 | 125 | 0.2 | [20 empty] | CEC Title24-2013 | JA4-10 | Masonry Units Solid | Concrete - Solid Grout - 125 lb/ft3 - 8 in. | [5 empty] | From CEC Title24 2013
Concrete Paver | StandardOpaqueMaterial | MediumRough | 0.38 | 4.5024 | 0.084399 | 144 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Masonry Materials | Concrete Paver | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 1.8396 | 7.3386 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 1.4496 | 9.6578 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.05 | 14.2857 | 120.2 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 0.8496 | 18.8324 | 112.75 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.63 | 28.5714 | 100.33 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 2.5704 | 5.2521 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 2.01 | 6.9652 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 1.4796 | 10.1379 | 120.2 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 1.1904 | 13.4409 | 112.75 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 0.9 | 20 | 100.33 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 100% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.85118 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 14.7504 | 0.94913 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 11.9904 | 1.251 | 120.2 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 10.3404 | 1.5473 | 112.75 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 8.3604 | 2.153 | 100.33 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 15.8604 | 0.85118 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 25.1796 | 0.55601 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 31.5096 | 0.47605 | 120.2 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 38.37 | 0.41699 | 112.75 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 54.0504 | 0.33302 | 100.33 | 0.13 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 80% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 10.7904 | 1.2511 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.4493 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.32 | 2.0492 | 120.2 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.0396 | 2.6492 | 112.75 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 4.7904 | 3.7575 | 100.33 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - No Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | StandardOpaqueMaterial | MediumRough | 13.5 | 11.7396 | 1.15 | 133.44 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 1 1/2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | StandardOpaqueMaterial | MediumRough | 14 | 9.66 | 1.4493 | 128.71 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 2 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | StandardOpaqueMaterial | MediumRough | 15 | 7.6896 | 1.9507 | 120.2 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 3 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | StandardOpaqueMaterial | MediumRough | 16 | 6.5304 | 2.4501 | 112.75 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 4 in. | [5 empty] | From CEC Title24 2013
Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | StandardOpaqueMaterial | MediumRough | 18 | 5.0604 | 3.557 | 100.33 | 0.12 | [20 empty] | CEC Title24-2013 | JA4-10 | Concrete Sandwich Panel | Concrete Sandwich Panel - 90% Ins. Layer - Steel in Ins. - Ins. 6 in. | [5 empty] | From CEC Title24 2013
Concrete/Sand Aggregate - 6 in. | StandardOpaqueMaterial | Smooth | 6.01 | 4.29 | 1.4009 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Concrete/Sand Aggregate - 6 in. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.9 | 2.5222 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - No Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.26196 | 12.4828 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R10 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.25296 | 17.6708 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R15 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.25308 | 22.404 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R20 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.724 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R25 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.4879 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R30 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2814 | 6.5032 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R4 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.27 | 9.4444 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Double glass with no low e coatings - R7 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 1.1796 | 1.9244 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.27312 | 11.9728 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.2628 | 17.0091 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.2592 | 21.875 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.25512 | 26.9285 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.25692 | 31.4106 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.3096 | 5.9109 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.28476 | 8.9549 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.78 | 2.9103 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - No Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.25452 | 12.8477 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R10 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.24804 | 18.0213 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R15 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.24696 | 22.9592 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R20 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.2478 | 27.724 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R25 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 0.2484 | 32.4879 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R30 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.2652 | 6.9005 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R4 Ins. | [5 empty] | From CEC Title24 2013
Continuous Ins. - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.25752 | 9.9021 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Continuous Ins. - Triple or low e glass - R7 Ins. | [5 empty] | From CEC Title24 2013
CP02 CARPET PAD | MasslessOpaqueMaterial | VeryRough |  |  | 1.2292 |  |  | 0.9 | 0.7 | 0.8
Douglas Fir-Larch - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.9804 | 1.02 | 34.88 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Douglas Fir-Larch - 1 in. | [5 empty] | From CEC Title24 2013
ECABS-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.814 | 0.086 | 0.086 | 0.847 | 0.099 | 0.099 | 0 | 0.84 | 0.1 | 1 | FALSE
ECABS-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.111 | 0.179 | 0.179 | 0.128 | 0.081 | 0.081 | 0 | 0.84 | 0.1 | 1 | FALSE
ECREF-1 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.84 | 1 | FALSE
ECREF-2 BLEACHED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.694 | 0.168 | 0.168 | 0.818 | 0.11 | 0.11 | 0 | 0.84 | 0.1 | 1 | FALSE
ECREF-2 COLORED 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.099 | 0.219 | 0.219 | 0.155 | 0.073 | 0.073 | 0 | 0.84 | 0.1 | 1 | FALSE
Expanded perlite - organic bonded - 1 1/2 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.36 | 4.1667 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 1/2 in. R4.2 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 1 in. R2.8 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.36 | 2.7778 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 1 in. R2.8 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 2 in. R5.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.36 | 5.5556 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 2 in. R5.6 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 3 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.36 | 8.3333 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3 in. R8.3 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 3/4 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.36 | 2.0833 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 3/4 in. R2.1 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 4 in. R11 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.36 | 11.1111 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 4 in. R11 | [5 empty] | From CEC Title24 2013
Expanded perlite - organic bonded - 6 in. R17 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.36 | 16.6667 | 1 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded perlite - organic bonded - 6 in. R17 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.24 | 6.25 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 1/2 in. R6.3 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.24 | 5.2083 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 1/4 in. R5.2 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | StandardOpaqueMaterial | MediumSmooth | 1.94 | 0.24 | 8.0833 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 15/16 in. R8.1 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.24 | 7.2917 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 3/4 in. R7.3 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | StandardOpaqueMaterial | MediumSmooth | 1.92 | 0.24 | 8 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1 7/8 in. R8.0 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1 in. R4.2 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.24 | 4.1667 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1 in. R4.2 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1/2 in. R2.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.24 | 2.0833 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 1/2 in. R2.1 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 1/4 in. R1.0 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.24 | 1.0417 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 1/4 in. R1.0 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 2 2/5 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.4 | 0.24 | 10 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 2/5 in. R10 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 2 7/16 in. R10 | StandardOpaqueMaterial | MediumSmooth | 2.43 | 0.24 | 10.125 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 2 7/16 in. R10 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 2 in. R8.3 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.24 | 8.3333 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polystyrene - EPS - 2 in. R8.3 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 3 1/2 in. R15 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.24 | 14.5833 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/2 in. R15 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 3 1/3 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.35 | 0.24 | 13.9583 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 1/3 in. R14 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 3 2/5 in. R14 | StandardOpaqueMaterial | MediumSmooth | 3.39 | 0.24 | 14.125 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 2/5 in. R14 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 3 in. R13 | StandardOpaqueMaterial | MediumSmooth | 3.01 | 0.24 | 12.5417 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3 in. R13 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 3/4 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.24 | 3.125 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 3/4 in. R3.1 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 4 1/16 in. R17 | StandardOpaqueMaterial | MediumSmooth | 4.05 | 0.24 | 16.875 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 1/16 in. R17 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 4 7/10 in. R20 | StandardOpaqueMaterial | MediumSmooth | 4.71 | 0.24 | 19.625 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 4 7/10 in. R20 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 5 19/20 in. R25 | StandardOpaqueMaterial | MediumSmooth | 5.96 | 0.24 | 24.8333 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 19/20 in. R25 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 5 2/5 in. R22 | StandardOpaqueMaterial | MediumSmooth | 5.2 | 0.24 | 21.6667 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 5 2/5 in. R22 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 6 1/10 in. R25 | StandardOpaqueMaterial | MediumSmooth | 6.11 | 0.24 | 25.4583 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 1/10 in. R25 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 6 7/8 in. R29 | StandardOpaqueMaterial | MediumSmooth | 6.87 | 0.24 | 28.625 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 6 7/8 in. R29 | [5 empty] | From CEC Title24 2013
Expanded Polystyrene - EPS - 8 3/5 in. R35 | StandardOpaqueMaterial | MediumSmooth | 8.38 | 0.24 | 34.9167 | 1.2 | 0.27 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Expanded Polystyrene - EPS - 8 3/5 in. R35 | [5 empty] | From CEC Title24 2013
Expanded Polyurethane - 1 1/4 in. R7.8 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.1596 | 7.8321 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 1/4 in. R7.8 | [5 empty] | From CEC Title24 2013
Expanded Polyurethane - 1 in. R6.3 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.1596 | 6.2657 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1 in. R6.3 | [5 empty] | From CEC Title24 2013
Expanded Polyurethane - 1/2 in. R3.1 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.1596 | 3.1328 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 1/2 in. R3.1 | [5 empty] | From CEC Title24 2013
Expanded Polyurethane - 2 in. R12.6 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.1596 | 12.5313 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 2 in. R12.6 | [5 empty] | From CEC Title24 2013
Expanded Polyurethane - 3/4 in. R4.7 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.1596 | 4.6992 | 1 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | Expanded Polyurethane - 3/4 in. R4.7 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.2 | 7.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/2 in. R7.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.2 | 6.25 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 1/4 in. R6.25 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | StandardOpaqueMaterial | MediumSmooth | 1.75 | 0.2 | 8.75 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 3/4 in. R8.75 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1 7/8 in. R9.37 | StandardOpaqueMaterial | MediumSmooth | 1.88 | 0.2 | 9.4 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 7/8 in. R9.37 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1 in. R5.00 | StandardOpaqueMaterial | MediumSmooth | 1 | 0.2 | 5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1 in. R5.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1/2 in. R2.50 | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.2 | 2.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/2 in. R2.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 1/4 in. R1.25 | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.2 | 1.25 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 1/4 in. R1.25 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | StandardOpaqueMaterial | MediumSmooth | 2.5 | 0.2 | 12.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 1/2 in. R12.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 2 in. R10.00 | StandardOpaqueMaterial | MediumSmooth | 2 | 0.2 | 10 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 2 in. R10.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | StandardOpaqueMaterial | MediumSmooth | 3.5 | 0.2 | 17.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 1/2 in. R17.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 3 in. R15.00 | StandardOpaqueMaterial | MediumSmooth | 3 | 0.2 | 15 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3 in. R15.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 3/4 in. R3.75 | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.2 | 3.75 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 3/4 in. R3.75 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | StandardOpaqueMaterial | MediumSmooth | 4.5 | 0.2 | 22.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 1/2 in. R22.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 4 in. R20.00 | StandardOpaqueMaterial | MediumSmooth | 4 | 0.2 | 20 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 4 in. R20.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | StandardOpaqueMaterial | MediumSmooth | 5.5 | 0.2 | 27.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 1/2 in. R27.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 5 in. R25.00 | StandardOpaqueMaterial | MediumSmooth | 5 | 0.2 | 25 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 5 in. R25.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | StandardOpaqueMaterial | MediumSmooth | 6.5 | 0.2 | 32.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 1/2 in. R32.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 6 in. R30.00 | StandardOpaqueMaterial | MediumSmooth | 6 | 0.2 | 30 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 6 in. R30.00 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | StandardOpaqueMaterial | MediumSmooth | 8.5 | 0.2 | 42.5 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 1/2 in. R42.50 | [5 empty] | From CEC Title24 2013
Extruded Polystyrene - XPS - 8 in. R40.00 | StandardOpaqueMaterial | MediumSmooth | 8 | 0.2 | 40 | 1.3 | 0.35 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Board | Extruded Polystyrene - XPS - 8 in. R40.00 | [5 empty] | From CEC Title24 2013
F04 Wall air space resistance | AirGap |  |  | 46.2231 | 0.021634
F05 Ceiling air space resistance | AirGap |  |  | 38.5193 | 0.025961
F08 Metal surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
F16 Acoustic tile | StandardOpaqueMaterial | MediumSmooth | 0.75197 | 0.41601 | 1.8076 | 22.9735 | 0.14092 | 0.9 | 0.3 | 0.3
Fiber cement board - 63 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.2996 | 0.23853 | 63 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 63 lb/ft3 - 1/3 in. | [5 empty] | From CEC Title24 2013
Fiber cement board - 88 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.47 | 1.7004 | 0.27641 | 88 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Fiber cement board - 88 lb/ft3 - 1/3 in. | StandardOpaqueMaterial | Smooth | 0.31 | 1.7004 | 0.18231 | 88 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiber cement board - 88 lb/ft3 - 1/3 in. | [5 empty] | From CEC Title24 2013
Fiberboard sheathing - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.4896 | 1.0212 | 24.96 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Fiberboard sheathing - 1/2 in. | [5 empty] | From CEC Title24 2013
Fixed Window 2.00/0.40/0.31 | SimpleGlazing | [10 empty] | 0.35 | 0.4 | 0.31
Fixed Window 2.00/0.45/0.35 | SimpleGlazing | [10 empty] | 0.35 | 0.45 | 0.35
Fixed Window 2.30/0.40/0.31 | SimpleGlazing | [10 empty] | 0.4 | 0.4 | 0.31
Fixed Window 2.56/0.45/0.35 | SimpleGlazing | [10 empty] | 0.45 | 0.45 | 0.35
Fixed Window 2.62/0.30/0.21 | SimpleGlazing | [10 empty] | 0.45998 | 0.3 | 0.21
Fixed Window 2.67/0.30/0.21 | SimpleGlazing | [10 empty] | 0.46998 | 0.49 | 0.38
Fixed Window 2.96/0.39/0.31 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.31
Fixed Window 2.96/0.49/0.41 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.41
Fixed Window 2.96/0.62/0.54 | SimpleGlazing | [10 empty] | 0.51998 | 0.62 | 0.54
Fixed Window 3.12/0.40/0.31 | SimpleGlazing | [10 empty] | 0.55 | 0.4 | 0.31
Fixed Window 3.24/0.25/0.16 | SimpleGlazing | [10 empty] | 0.56997 | 0.25 | 0.16
Fixed Window 3.24/0.39/0.31 | SimpleGlazing | [10 empty] | 0.56997 | 0.39 | 0.31
Fixed Window 3.24/0.49/0.41 | SimpleGlazing | [10 empty] | 0.56997 | 0.49 | 0.41
Fixed Window 3.35/0.36/0.27 | SimpleGlazing | [10 empty] | 0.58997 | 0.36 | 0.27
Fixed Window 3.35/0.39/0.31 | SimpleGlazing | [10 empty] | 0.58997 | 0.39 | 0.31
Fixed Window 3.53/0.41/0.32 | SimpleGlazing | [10 empty] | 0.61997 | 0.41 | 0.32
Fixed Window 3.69/0.25/0.16 | SimpleGlazing | [10 empty] | 0.65 | 0.25 | 0.16
Fixed Window 3.69/0.70/0.60 | SimpleGlazing | [10 empty] | 0.65 | 0.7 | 0.6
Fixed Window 3.81/0.39/0.27 | SimpleGlazing | [10 empty] | 0.51998 | 0.39 | 0.27
Fixed Window 3.81/0.49/0.38 | SimpleGlazing | [10 empty] | 0.51998 | 0.49 | 0.38
Fixed Window 4.09/0.26/0.13 | SimpleGlazing | [10 empty] | 0.71997 | 0.25 | 0.13
Fixed Window 4.09/0.36/0.23 | SimpleGlazing | [10 empty] | 0.71997 | 0.36 | 0.23
Fixed Window 4.09/0.39/0.25 | SimpleGlazing | [10 empty] | 0.71997 | 0.39 | 0.25
Fixed Window 4.26/0.25/0.16 | SimpleGlazing | [10 empty] | 0.75 | 0.25 | 0.16
Fixed Window 5.84/0.25/0.11 | SimpleGlazing | [10 empty] | 1.0285 | 0.25 | 0.11
Fixed Window 5.84/0.39/0.22 | SimpleGlazing | [10 empty] | 1.0285 | 0.39 | 0.22
Fixed Window 5.84/0.44/0.27 | SimpleGlazing | [10 empty] | 1.0285 | 0.44 | 0.27
Fixed Window 5.84/0.54/0.38 | SimpleGlazing | [10 empty] | 1.0285 | 0.54 | 0.38
Fixed Window 5.84/0.61/0.47 | SimpleGlazing | [10 empty] | 1.0285 | 0.61 | 0.47
Fixed Window 5.84/0.70/0.60 | SimpleGlazing | [10 empty] | 1.0285 | 0.7 | 0.6
G01 13mm gypsum board | StandardOpaqueMaterial | Smooth | 0.5 | 1.1096 | 0.45063 | 49.9424 | 0.26052 | 0.9 | 0.7 | 0.5
G01a 19mm gypsum board | StandardOpaqueMaterial | MediumSmooth | 0.74803 | 1.1094 | 0.67429 | 49.9424 | 0.26034 | 0.9 | 0.4 | 0.4
G05 25mm wood | StandardOpaqueMaterial | MediumSmooth | 1 | 1.04 | 0.96152 | 37.9562 | 0.38932 | 0.9 | 0.5 | 0.5
Gap_1_W_0_0018 | Gas |  | 0.070866 | [7 empty] | Air
Gap_1_W_0_0024 | Gas |  | 0.094488 | [7 empty] | Air
Gap_1_W_0_0025 | Gas |  | 0.098425 | [7 empty] | Air
Gap_1_W_0_0032 | Gas |  | 0.12598 | [7 empty] | Air
Gap_1_W_0_0038 | Gas |  | 0.14961 | [7 empty] | Air
Gap_1_W_0_0042 | Gas |  | 0.16535 | [7 empty] | Air
Gap_1_W_0_0043 | Gas |  | 0.16929 | [7 empty] | Air
Glass fiber batt - 10 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 10 | 0.3336 | 29.976 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 10 in. R30 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 12 in. R38 (CEC Default) | StandardOpaqueMaterial | MediumRough | 12 | 0.3156 | 38.0228 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 12 in. R38 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 3 1/2 in. R11 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.318 | 11.0063 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R11 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 3 1/2 in. R13 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2688 | 13.0208 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R13 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 3 1/2 in. R15 (CEC Default) | StandardOpaqueMaterial | MediumRough | 3.5 | 0.2328 | 15.0344 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 3 1/2 in. R15 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.3 | 15 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 1/2 in. | [5 empty] | From CEC Title24 2013
Glass fiber batt - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.3 | 13.3333 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 4 in. | [5 empty] | From CEC Title24 2013
Glass fiber batt - 5 1/2 in. R19 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.306 | 17.9739 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R19 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 5 1/2 in. R21 (CEC Default) | StandardOpaqueMaterial | MediumRough | 5.5 | 0.2616 | 21.0245 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 5 1/2 in. R21 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.3 | 16.6667 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 5 in. | [5 empty] | From CEC Title24 2013
Glass fiber batt - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.3 | 21.6667 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Glass fiber batt - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.3 | 20 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Batt | Glass fiber batt - 6 in. | [5 empty] | From CEC Title24 2013
Glass fiber batt - 7 1/4 in. R25 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.3024 | 23.9749 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R25 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 7 1/4 in. R30 (CEC Default) | StandardOpaqueMaterial | MediumRough | 7.25 | 0.2904 | 24.9656 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 7 1/4 in. R30 (CEC Default) | [5 empty] | From CEC Title24 2013
Glass fiber batt - 8 1/4 in. R30C (CEC Default) | StandardOpaqueMaterial | MediumRough | 8.25 | 0.2748 | 30.0218 | 0.7 | 0.2 | [20 empty] | CEC Title24-2013 | CEC RJ | Insulation Batt | Glass fiber batt - 8 1/4 in. R30C (CEC Default) | [5 empty] | From CEC Title24 2013
Glass_2010F_LayerAvg | StandardGlazing |  | 0.087008 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.43429 | 0.41837 | 0.34107 | 0.79758 | 0.043577 | 0.056031 | 0 | 0.042274 | 0.84 | 1 | FALSE
Glass_2022F_LayerAvg | StandardGlazing |  | 0.15354 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.3559 | 0.39409 | 0.26565 | 0.67769 | 0.042734 | 0.05547 | 0 | 0.046 | 0.84 | 1 | FALSE
Glass_2027F_LayerAvg | StandardGlazing |  | 0.15748 | 6.9335 | [10 empty] | SpectralAverage | 0.36974 | 0.47007 | 0.34093 | 0.76522 | 0.0546 | 0.073741 | 0 | 0.03675 | 0.84 | 1 | FALSE
Glass_2052_LayerAvg | StandardGlazing |  | 0.32953 | 6.9335 | [10 empty] | SpectralAverage | 0.50777 | 0.054228 | 0.054493 | 0.58683 | 0.05805 | 0.058397 | 0 | 0.84 | 0.84 | 1 | FALSE
Glass_2175_LayerAvg | StandardGlazing |  | 0.33858 | 6.9335 | 0.14423 | [9 empty] | SpectralAverage | 0.16776 | 0.21761 | 0.43798 | 0.41604 | 0.078729 | 0.10654 | 0 | 0.84 | 0.84 | 1 | FALSE
GREEN 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.635 | 0.063 | 0.063 | 0.822 | 0.075 | 0.075 | 0 | 0.84 | 0.84 | 1 | FALSE
GREEN 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.487 | 0.056 | 0.056 | 0.749 | 0.07 | 0.07 | 0 | 0.84 | 0.84 | 1 | FALSE
GREY 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.455 | 0.053 | 0.053 | 0.431 | 0.052 | 0.052 | 0 | 0.84 | 0.84 | 1 | FALSE
Ground_Floor_R11_T2013 | StandardOpaqueMaterial | Smooth | 1.7412 | 0.15963 | 10.91 | 1 | 0.27 | 0.9 | 0.7 | 0.8
Ground_Floor_R17_T2013 | StandardOpaqueMaterial | Smooth | 2.7132 | 0.15963 | 17.66 | 1 | 0.27 | 0.9 | 0.7 | 0.8
Ground_Floor_R22_T2013 | StandardOpaqueMaterial | Smooth | 3.5112 | 0.15963 | 22.47 | 1 | 0.27 | 0.9 | 0.7 | 0.8
Gypsum Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1 | 0.45453 | 40 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 1/2 in. | [5 empty] | From CEC Title24 2013
Gypsum Board - 1/2 in. CBES | StandardOpaqueMaterial | Smooth | 0.5 | 1.1101 |  | 40 | 0.27 | 0.9 | 0.7 | 0.8
Gypsum Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1 | 0.68179 | 40 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/4 in. | [5 empty] | From CEC Title24 2013
Gypsum Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 1.1 | 0.34544 | 40 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 3/8 in. | [5 empty] | From CEC Title24 2013
Gypsum Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 1.1 | 0.57271 | 40 | 0.27 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Gypsum Board - 5/8 in. | [5 empty] | From CEC Title24 2013
Gypsum Or Plaster Board - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.37402 | 4.0214 | 0.093006 | 49.9424 | 0.26034 | 0.9 | 0.7 | 0.7
Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 2.4 | 1.6667 | 53.1 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 3 cells - 4 in. x 12 in. x 30 in. - 4 in. | [5 empty] | From CEC Title24 2013
Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.22 | 1.3514 | 53.1 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - 4 cells - 3 in. x 12 in. x 30 in. - 3 in. | [5 empty] | From CEC Title24 2013
Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in. | StandardOpaqueMaterial | MediumRough | 3 | 2.3796 | 1.2607 | 62.4 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Gypsum partition block - solid - 3 in. x 12 in. x 30 in. - 3 in. | [5 empty] | From CEC Title24 2013
Gypsum plaster - 80 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 3.2004 | 0.15623 | 80 | 0.26 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Gypsum plaster - 80 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 3.2004 | 0.19685 | 80 | 0.26 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - 80 lb/ft3 - 5/8 in. | [5 empty] | From CEC Title24 2013
Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 2.6004 | 0.28842 | 70 | 0.26 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 70 lb/ft3 - 3/4 in. | [5 empty] | From CEC Title24 2013
Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 3.2004 | 0.23435 | 80 | 0.26 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Gypsum plaster - on metal lath 80 lb/ft3 - 3/4 in. | [5 empty] | From CEC Title24 2013
Hard Board - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.72 | 1.0417 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Hard Board - 3/4 in. | [5 empty] | From CEC Title24 2013
Hardboard - HDF - 50 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.7296 | 0.68531 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Hardboard - HDF - 50 lb/ft3 - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 0.7296 | 1.028 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/4 in. | [5 empty] | From CEC Title24 2013
Hardboard - HDF - 50 lb/ft3 - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 0.7296 | 0.52083 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 3/8 in. | [5 empty] | From CEC Title24 2013
Hardboard - HDF - 50 lb/ft3 - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 0.7296 | 0.86349 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Hardboard - HDF - 50 lb/ft3 - 5/8 in. | [5 empty] | From CEC Title24 2013
Hardwood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1604 | 0.86177 | 42.43 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1 in. | [5 empty] | From CEC Title24 2013
Hardwood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.1604 | 0.43089 | 42.43 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 1/2 in. | [5 empty] | From CEC Title24 2013
Hardwood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 1.1604 | 0.64633 | 42.43 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Hardwood - 3/4 in. | [5 empty] | From CEC Title24 2013
HB Part. Brd - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 1.18 | 0.63561 | 50 | 0.31 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | HB Part. Brd - 3/4 in. | [5 empty] | From CEC Title24 2013
HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0915 | 0.43997 | 139.8387 | 0.2 | 0.9 | 0.7 | 0.7
HW CONCRETE 8 in | StandardOpaqueMaterial | Rough | 8 | 9.0915 | 0.87994 | 139.8387 | 0.2 | 0.9 | 0.7 | 0.7
I01 25mm insulation board | StandardOpaqueMaterial | MediumRough | 1 | 0.208 | 4.8076 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
I02 50mm insulation board | StandardOpaqueMaterial | MediumRough | 2 | 0.208 | 9.6152 | 2.6844 | 0.289 | 0.9 | 0.6 | 0.6
IEAD NonRes Roof Insulation-1.76 | StandardOpaqueMaterial | MediumRough | 2.9126 | 0.33974 | 8.5731 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
IEAD Roof Insulation R-3.47 IP | StandardOpaqueMaterial | MediumRough | 1.1788 | 0.33974 | 3.4698 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 9 | 0.4704 | 19.1327 | 100.33 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 11 | 0.57 | 19.2982 | 109.36 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 1 1/2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 11 | 0.51648 | 21.298 | 76.81 | 0.23 | [20 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 13 | 0.60612 | 21.4479 | 86.54 | 0.22 | [20 empty] | CEC Title24-2013 | CEC RJ | ICF Wall | Insulating Concrete Forms - 2 1/2 in. EPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.6096 | 16.4042 | 90.4 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.72 | 16.6667 | 100.33 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. EPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4404 | 22.7066 | 90.4 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5196 | 23.0947 | 100.33 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 10 | 0.4704 | 21.2585 | 90.4 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 12 | 0.57 | 21.0526 | 100.33 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 2 in. XPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.5004 | 23.9808 | 75.5 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.57 | 24.5614 | 86.14 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. EPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 12 | 0.39 | 30.7692 | 75.5 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 14 | 0.45 | 31.1111 | 86.14 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 3 in. XPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 15 | 0.3504 | 42.8082 | 60.6 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 17 | 0.3996 | 42.5425 | 71.12 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 1/2 in. Polyurethane Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.4296 | 32.5885 | 64.86 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.5004 | 31.9744 | 75.5 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. EPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | StandardOpaqueMaterial | Smooth | 14 | 0.3504 | 39.9543 | 64.86 | 0.23 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 6 in. | [5 empty] | From CEC Title24 2013
Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | StandardOpaqueMaterial | Smooth | 16 | 0.39 | 41.0256 | 75.5 | 0.22 | [20 empty] | CEC Title24-2013 | JA4-10 | ICF Wall | Insulating Concrete Forms - 4 in. XPS Ins. each side - concrete 8 in. | [5 empty] | From CEC Title24 2013
Insulation 1m | StandardOpaqueMaterial | Smooth | 39.37 | 0.13876 |  | 1 | 0.27 | 0.9 | 0.7 | 0.8
Interior Wall Addi Insul | StandardOpaqueMaterial | MediumRough | 1e-06 | 0.29994 | 3.334e-06 | 1.4 | 0.19987 | 0.9 | 0.7 | 0.7
Light Roof - 2/5 in. | StandardOpaqueMaterial | VeryRough | 0.2 | 2.4012 | 0.083292 | 120 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Light Roof - 2/5 in. | [5 empty] | From CEC Title24 2013
Linoleum/cork tile - 1/4 in. | StandardOpaqueMaterial | MediumRough | 0.25 | 0.51 | 0.4902 | 29 | 0.45 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Linoleum/cork tile - 1/4 in. | [5 empty] | From CEC Title24 2013
LoE CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.6 | 0.17 | 0.22 | 0.84 | 0.055 | 0.078 | 0 | 0.84 | 0.1 | 1 | FALSE
LoE SPEC SEL CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.45 | 0.34 | 0.37 | 0.78 | 0.07 | 0.06 | 0 | 0.84 | 0.03 | 1 | FALSE
LoE SPEC SEL CLEAR 6MM Rev | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.43 | 0.42 | 0.3 | 0.77 | 0.06 | 0.07 | 0 | 0.03 | 0.84 | 1 | FALSE
LoE SPEC SEL TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.26 | 0.14 | 0.41 | 0.46 | 0.06 | 0.04 | 0 | 0.84 | 0.03 | 1 | FALSE
LoE TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.36 | 0.093 | 0.2 | 0.5 | 0.035 | 0.054 | 0 | 0.84 | 0.1 | 1 | FALSE
Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | StandardOpaqueMaterial | Rough | 13.75 | 0.336 | 40.9226 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 13 3/4 in. | [5 empty] | From CEC Title24 2013
Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.336 | 11.9048 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.336 | 19.3452 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | StandardOpaqueMaterial | Rough | 7.5 | 0.336 | 22.3214 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 7 1/2 in. | [5 empty] | From CEC Title24 2013
Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | StandardOpaqueMaterial | Rough | 8.25 | 0.336 | 24.5536 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - 2 lb/ft3 - 8 1/4 in. | [5 empty] | From CEC Title24 2013
Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.336 | 10.4167 | 2 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Loose Fill | Loose fill - Mineral fiber - closed sidewalls - 3 1/2 in. | [5 empty] | From CEC Title24 2013
M01 100mm brick | StandardOpaqueMaterial | MediumRough | 4 | 6.1708 | 0.64822 | 119.8617 | 0.18869 | 0.9 | 0.7 | 0.7
M11 100mm lightweight concrete | StandardOpaqueMaterial | MediumRough | 4 | 3.6747 | 1.0885 | 79.9078 | 0.20063 | 0.9 | 0.5 | 0.5
M15 200mm heavyweight concrete | StandardOpaqueMaterial | MediumRough | 8 | 13.5203 | 0.5917 | 139.8386 | 0.21496 | 0.9 | 0.5 | 0.5
Maple - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.14 | 0.87719 | 41.87 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Maple - 1 in. | [5 empty] | From CEC Title24 2013
Mass NonRes Wall Insulation-0.43 | StandardOpaqueMaterial | MediumRough | 0.017196 | 0.33974 | 0.050616 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mass Wall Insulation R-4.23 IP | StandardOpaqueMaterial | MediumRough | 1.4385 | 0.33974 | 4.234 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Mastic asphalt (heavy - 20% grit) - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 1.2996 | 0.76947 | 59 | 0.22 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Mastic asphalt (heavy - 20% grit) - 1 in. | [5 empty] | From CEC Title24 2013
MAT-CC05 4 HW CONCRETE | StandardOpaqueMaterial | Rough | 4 | 9.0898 | 0.44005 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-CC05 8 HW CONCRETE | StandardOpaqueMaterial | Rough | 8 | 9.0898 | 0.88011 | 139.8386 | 0.19987 | 0.9 | 0.85 | 0.85
MAT-SHEATH | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
Metal Building Semi-Cond Wall Insulation-0.54 | StandardOpaqueMaterial | MediumRough | 0.60417 | 0.33974 | 1.7783 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Building Wall Insulation R-4.14 IP | StandardOpaqueMaterial | MediumRough | 1.4044 | 0.33974 | 4.1339 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Deck - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0.00019879 | 488.22 | 0.12 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Deck - 1/16 in. | [5 empty] | From CEC Title24 2013
Metal Decking | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 9.383 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 9_25in | 2x10 | 30 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 10.756 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 11_25in | 2x12 | 38 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 0 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 11 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 5.854 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 13 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.92 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 5_5in | 2x6 | 19 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 7.414 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 19 | From CEC Title24 2013
Metal Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 7.815 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor16inOC | 7_25in | 2x8 | 22 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 12.443 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 9_25in | 2x10 | 30 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 14.569 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 11_25in | 2x12 | 38 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x6 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.003 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 0 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.576 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 11 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.544 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 13 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.037 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 5_5in | 2x6 | 19 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.564 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 19 | From CEC Title24 2013
Metal Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 10.336 | [22 empty] | CEC Title24-2013 |  | Metal Framed Floor |  | Metal | Floor24inOC | 7_25in | 2x8 | 22 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 10.16 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 10.92 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.34 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 13_25In | 2x14 | 38 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.01 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 6.52 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.39 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 6.96 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.16 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 15 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.26 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Metal Framed Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 9.01 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof16inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 12.97 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.13 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 14.65 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 16.44 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 17.13 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 13_25In | 2x14 | 38 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.27 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.68 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 8.06 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.61 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.36 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 9.89 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 15 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.31 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 10.76 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Metal Framed Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 11.42 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | Roof24inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.643 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 0 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 2.924 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 11 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.068 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 13 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.199 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 15 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.309 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 3_5in | 2x4 | 5 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 3.924 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 19 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.078 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 5_5in | 2x6 | 21 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 19 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 4.71 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 22 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 4.789 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 25 | From CEC Title24 2013
Metal Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 4.829 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall16inOC | 7_25in | 2x8 | 30 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x4 - R0 ins. | MasslessOpaqueMaterial |  |  |  | 0.658 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 0 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 3.222 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 11 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 3.386 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 13 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 3.536 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 15 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x4 - R5 ins. | MasslessOpaqueMaterial |  |  |  | 1.463 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 3_5in | 2x4 | 5 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.558 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 19 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 4.671 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 5_5in | 2x6 | 21 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 4.996 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 19 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 5.171 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 22 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 5.263 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 25 | From CEC Title24 2013
Metal Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 5.309 | [22 empty] | CEC Title24-2013 |  | Metal Framed Wall |  | Metal | Wall24inOC | 7_25in | 2x8 | 30 | From CEC Title24 2013
Metal Insulated Panels - 2 1/2 in. | StandardOpaqueMaterial | Smooth | 2.5 | 0.16644 | 15.0204 | 28.47 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 1/2 in. | [5 empty] | From CEC Title24 2013
Metal Insulated Panels - 2 in. | StandardOpaqueMaterial | Smooth | 2 | 0.16704 | 11.9732 | 34.87 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 2 in. | [5 empty] | From CEC Title24 2013
Metal Insulated Panels - 3 in. | StandardOpaqueMaterial | Smooth | 3 | 0.16656 | 18.0115 | 24.11 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 3 in. | [5 empty] | From CEC Title24 2013
Metal Insulated Panels - 4 in. | StandardOpaqueMaterial | Smooth | 4 | 0.16992 | 23.5405 | 18.54 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 4 in. | [5 empty] | From CEC Title24 2013
Metal Insulated Panels - 5 in. | StandardOpaqueMaterial | Smooth | 5 | 0.1698 | 29.4464 | 15.14 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 5 in. | [5 empty] | From CEC Title24 2013
Metal Insulated Panels - 6 in. | StandardOpaqueMaterial | Smooth | 6 | 0.16584 | 36.1795 | 12.84 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Metal Insulated Panel Wall | Metal Insulated Panels - 6 in. | [5 empty] | From CEC Title24 2013
Metal Roof Insulation R-5.21 IP | StandardOpaqueMaterial | MediumRough | 1.7692 | 0.33974 | 5.2076 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Roof Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
Metal Roof Surface - Cool Roof | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.75 | 0.37 | 0.7 | [26 empty] | From LA city ordinance
Metal Roof Surface - Highly Reflective | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.75 | 0.45 | 0.7
Metal Roofing | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.9 | 0.6 | 0.6
Metal Roofing - Cool Roof | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.75 | 0.37 | 0.6 | [26 empty] | From LA city ordinance
Metal Roofing - Highly Reflective | StandardOpaqueMaterial | MediumSmooth | 0.059055 | 312.0478 | 0.00018925 | 479.4467 | 0.099933 | 0.75 | 0.45 | 0.6
Metal Screw Down Roof - No Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 5.756 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 10 | From CEC Title24 2013
Metal Screw Down Roof - No Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 6.414 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 11 | From CEC Title24 2013
Metal Screw Down Roof - No Thrml Blk - R13ins. | MasslessOpaqueMaterial |  |  |  | 6.912 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 13 | From CEC Title24 2013
Metal Screw Down Roof - No Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 8.654 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 16 | From CEC Title24 2013
Metal Screw Down Roof - No Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 9.424 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalScrewDown | NA | NA | 19 | From CEC Title24 2013
Metal Semi-Cond Roof Insulation-1.05 | StandardOpaqueMaterial | MediumRough | 1.6641 | 0.33974 | 4.8981 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Metal Siding | StandardOpaqueMaterial | Smooth | 0.059055 | 311.7289 | 0.00018944 | 479.9998 | 0.097927 | 0.9 | 0.7 | 0.7
Metal Siding - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 314.4 | 0.00019879 | 488.22 | 0.12 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Metal Siding - 1/16 in. | [5 empty] | From CEC Title24 2013
Metal Standing Seam - 1/16 in. | StandardOpaqueMaterial | Smooth | 0.0625 | 3.9996 | 0.015627 | 488.22 | 0.12 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Metal Standing Seam - 1/16 in. | [5 empty] | From CEC Title24 2013
Metal Standing Seam - 1/16 in. CBES | StandardOpaqueMaterial | MediumRough | 0.06 | 4.0241 |  | 488.22 | 0.12 | 0.85 | 0.37 | 0.85
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 15.093 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 20 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.613 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 21 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.461 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 23 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R10 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.451 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 29 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R11 Ins. | MasslessOpaqueMaterial |  |  |  | 15.887 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 22 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 16.764 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 24 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R11 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 18.828 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 30 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R13 Ins. | MasslessOpaqueMaterial |  |  |  | 17.402 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 26 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R13 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 19.628 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 32 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R16 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.497 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 35 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Dbl Ins. Layer - R19 + R19 Ins. | MasslessOpaqueMaterial |  |  |  | 20.959 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 36 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - Ins. and Filled Cavity - R19 + R10 Ins. | MasslessOpaqueMaterial |  |  |  | 23.61 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeamFilledCavity | NA | NA | 29 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R10 ins. | MasslessOpaqueMaterial |  |  |  | 9.529 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 10 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.09 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 11 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.268 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 13 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R16 ins. | MasslessOpaqueMaterial |  |  |  | 13.109 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 16 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.605 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 19 | From CEC Title24 2013
Metal Standing Seam Roof - Thrml Blk - R6 ins. | MasslessOpaqueMaterial |  |  |  | 5.208 | [22 empty] | CEC Title24-2013 |  | Metal Building Roof |  | Metal | RoofMetalStandingSeam | NA | NA | 6 | From CEC Title24 2013
Metal Surface | StandardOpaqueMaterial | Smooth | 0.031496 | 313.9476 | 0.00010032 | 488.4364 | 0.11942 | 0.9 | 0.7 | 0.7
Mortar - Cement - 1 3/4 in. | StandardOpaqueMaterial | Smooth | 1.76 | 5.01 | 0.3513 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 3/4 in. | [5 empty] | From CEC Title24 2013
Mortar - Cement - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.20078 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Mortar - Cement - 1 in. | [5 empty] | From CEC Title24 2013
NACM_Carpet 3/4in | StandardOpaqueMaterial | Smooth | 0.75 | 0.34691 |  | 18 | 0.33 | 0.9 | 0.7 | 0.9
NACM_Concrete 4in_140lb/ft3 | StandardOpaqueMaterial | MediumRough | 4 | 13.5293 |  | 139.78 | 0.22 | 0.75 | 0.92 | 0.75
NACM_Gypsum Board 5/8in | StandardOpaqueMaterial | MediumRough | 0.63 | 1.1101 |  | 40 | 0.27 | 0.9 | 0.7 | 0.5
Nonres_Floor_Insulation | MasslessOpaqueMaterial | MediumSmooth |  |  | 16.37 |  |  | 0.9 | 0.7 | 0.7
Oak - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.1796 | 0.84774 | 43.93 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Oak - 1 in. | [5 empty] | From CEC Title24 2013
OSB - Oriented Strand Board - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.80593 | 41 | 0.45 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 1/2 in. | [5 empty] | From CEC Title24 2013
OSB - Oriented Strand Board - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.9096 | 0.82454 | 41 | 0.45 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 3/4 in. | [5 empty] | From CEC Title24 2013
OSB - Oriented Strand Board - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.7596 | 0.82938 | 41 | 0.45 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | OSB - Oriented Strand Board - 5/8 in. | [5 empty] | From CEC Title24 2013
Perlite board - 1 1/2 in. R3.8 | StandardOpaqueMaterial | Rough | 1.5 | 0.3996 | 3.7538 | 10 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 1/2 in. R3.8 | [5 empty] | From CEC Title24 2013
Perlite board - 1 in. R2.5 | StandardOpaqueMaterial | Rough | 1 | 0.3996 | 2.5025 | 10 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 1 in. R2.5 | [5 empty] | From CEC Title24 2013
Perlite board - 2 in. R5.0 | StandardOpaqueMaterial | Rough | 2 | 0.3996 | 5.005 | 10 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 2 in. R5.0 | [5 empty] | From CEC Title24 2013
Perlite board - 3/4 in. R1.9 | StandardOpaqueMaterial | Rough | 0.75 | 0.3996 | 1.8769 | 10 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Insulation Board | Perlite board - 3/4 in. R1.9 | [5 empty] | From CEC Title24 2013
Perlite plaster - 25 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.6 | 0.83333 | 25 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 25 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Perlite plaster - 38 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.2996 | 0.38473 | 38 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Perlite plaster - 38 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
Pine (oven-dried) - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.6396 | 1.5635 | 23 | 0.45 | [20 empty] | CEC Title24-2013 | AEC | Woods | Pine (oven-dried) - 1 in. | [5 empty] | From CEC Title24 2013
Plaster/Sand Aggregate - 1 in. | StandardOpaqueMaterial | Smooth | 1.01 | 5.0304 | 0.20078 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Plaster/Sand Aggregate - 1 in. | [5 empty] | From CEC Title24 2013
Plywood - 1 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 1.5 | 0.8004 | 1.8741 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/2 in. | [5 empty] | From CEC Title24 2013
Plywood - 1 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 1.25 | 0.8004 | 1.5617 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC RJ | Bldg Board and Siding | Plywood - 1 1/4 in. | [5 empty] | From CEC Title24 2013
Plywood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.8004 | 1.2494 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1 in. | [5 empty] | From CEC Title24 2013
Plywood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.8004 | 0.62469 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/2 in. | [5 empty] | From CEC Title24 2013
Plywood - 1/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.25 | 0.8004 | 0.31234 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 1/4 in. | [5 empty] | From CEC Title24 2013
Plywood - 3/4 in. | StandardOpaqueMaterial | MediumSmooth | 0.75 | 0.8004 | 0.93703 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/4 in. | [5 empty] | From CEC Title24 2013
Plywood - 3/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.38 | 0.8004 | 0.47476 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 3/8 in. | [5 empty] | From CEC Title24 2013
Plywood - 5/8 in. | StandardOpaqueMaterial | MediumSmooth | 0.63 | 0.8004 | 0.78711 | 30 | 0.45 | [20 empty] | CEC Title24-2013 | CEC Doug | Bldg Board and Siding | Plywood - 5/8 in. | [5 empty] | From CEC Title24 2013
Plywood - 5/8 in. CBES | StandardOpaqueMaterial | Smooth | 0.63 | 0.83257 |  | 30 | 0.45 | 0.9 | 0.7 | 0.7
Pulpboard or paper plaster - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 0.5004 | 0.9992 | 38 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Pulpboard or paper plaster - 1/2 in. | [5 empty] | From CEC Title24 2013
PYR B CLEAR 3MM | StandardGlazing |  | 0.11811 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.74 | 0.09 | 0.1 | 0.82 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE
PYR B CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.68 | 0.09 | 0.1 | 0.81 | 0.11 | 0.12 | 0 | 0.84 | 0.2 | 1 | FALSE
R_R30 | StandardOpaqueMaterial | Smooth | 4.7881 | 0.15963 | 30 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R_R38 | StandardOpaqueMaterial | Smooth | 6.0649 | 0.15963 | 38 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R_T24_2013_24.86 | StandardOpaqueMaterial | Smooth | 3.9677 | 0.15963 | 24.86 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R-24 Batt Wall - 8 in. R24 | StandardOpaqueMaterial | VeryRough | 8 | 0.3336 | 23.9808 | 1.19 | 0.23 | [20 empty] | CEC Title24-2013 | CEC Doug | Insulation Board | R-24 Batt Wall - 8 in. R24 | [5 empty] | From CEC Title24 2013
R1_R14.20 | StandardOpaqueMaterial | Smooth | 2.2664 | 0.15963 | 14.2 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R2_R12.90 | StandardOpaqueMaterial | Smooth | 2.0589 | 0.15963 | 12.9 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R3_R17.74 | StandardOpaqueMaterial | Smooth | 2.8313 | 0.15963 | 17.74 | 1 | 0.27 | 0.9 | 0.7 | 0.8
R4_R20.28 | StandardOpaqueMaterial | Smooth | 3.2367 | 0.15963 | 20.28 | 1 | 0.27 | 0.9 | 0.7 | 0.8
Rammed Earth | StandardOpaqueMaterial | Rough | 18 | 1.4796 | 12.1655 | 115 | 0.2 | [20 empty] | CEC Title24-2013 | CEC | Insulation Other | Rammed Earth | [5 empty] | From CEC Title24 2013
REF A CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.066 | 0.341 | 0.493 | 0.08 | 0.41 | 0.37 | 0 | 0.84 | 0.4 | 1 | FALSE
REF A CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.11 | 0.27 | 0.43 | 0.14 | 0.31 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE
REF A TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.06 | 0.13 | 0.42 | 0.09 | 0.14 | 0.35 | 0 | 0.84 | 0.47 | 1 | FALSE
REF B CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.24 | 0.16 | 0.32 | 0.3 | 0.16 | 0.29 | 0 | 0.84 | 0.6 | 1 | FALSE
REF B CLEAR LO 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.22 | 0.38 | 0.2 | 0.23 | 0.33 | 0 | 0.84 | 0.58 | 1 | FALSE
REF B TINT HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.15 | 0.09 | 0.33 | 0.18 | 0.08 | 0.28 | 0 | 0.84 | 0.6 | 1 | FALSE
REF B TINT MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.1 | 0.11 | 0.41 | 0.13 | 0.1 | 0.32 | 0 | 0.84 | 0.45 | 1 | FALSE
REF C CLEAR HI 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.2 | 0.16 | 0.39 | 0.22 | 0.17 | 0.35 | 0 | 0.84 | 0.55 | 1 | FALSE
REF C CLEAR MID 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.17 | 0.2 | 0.42 | 0.19 | 0.21 | 0.38 | 0 | 0.84 | 0.51 | 1 | FALSE
REF D CLEAR 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.429 | 0.308 | 0.379 | 0.334 | 0.453 | 0.505 | 0 | 0.84 | 0.82 | 1 | FALSE
REF D TINT 6MM | StandardGlazing |  | 0.23622 | 6.2401 | 0.16025 | [9 empty] | SpectralAverage | 0.3 | 0.14 | 0.36 | 0.25 | 0.18 | 0.45 | 0 | 0.84 | 0.82 | 1 | FALSE
Roof Gravel - 1 in. | StandardOpaqueMaterial | VeryRough | 1 | 9.9996 | 0.1 | 159.74 | 0.19 | [20 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1 in. | [5 empty] | From CEC Title24 2013
Roof Gravel - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 9.9996 | 0.050002 | 159.74 | 0.19 | [20 empty] | CEC Title24-2013 | CEC Doug | Roofing | Roof Gravel - 1/2 in. | [5 empty] | From CEC Title24 2013
Roof Insulation [18] | StandardOpaqueMaterial | MediumRough | 6.6654 | 0.33974 | 19.619 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Roof Membrane | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.33715 | 69.9998 | 0.34872 | 0.9 | 0.7 | 0.7
Roof Membrane - Cool Roof | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.33715 | 69.9998 | 0.34872 | 0.75 | 0.37 | 0.7 | [26 empty] | From LA city ordinance
Roof Membrane - Highly Reflective | StandardOpaqueMaterial | VeryRough | 0.37402 | 1.1094 | 0.33715 | 69.9998 | 0.34872 | 0.75 | 0.45 | 0.7
Roofing felt - 1/8 in. | StandardOpaqueMaterial | VeryRough | 0.13 | 8.3004 | 0.015662 | 141 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Building Membrane | Roofing felt - 1/8 in. | [5 empty] | From CEC Title24 2013
Rubber tile - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 0.3396 | 2.9446 | 119 | 0.48 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Rubber tile - 1 in. | [5 empty] | From CEC Title24 2013
Sand aggregate - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 5.4504 | 0.091736 | 105 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 1/2 in. | [5 empty] | From CEC Title24 2013
Sand aggregate - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.0796 | 0.14765 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/4 in. | [5 empty] | From CEC Title24 2013
Sand aggregate - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.1504 | 0.073781 | 116 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 3/8 in. | [5 empty] | From CEC Title24 2013
Sand aggregate - 5/8 in. | StandardOpaqueMaterial | Smooth | 0.63 | 5.6004 | 0.11249 | 105 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate - 5/8 in. | [5 empty] | From CEC Title24 2013
Sand aggregate on metal lath - 3/4 in. | StandardOpaqueMaterial | Smooth | 0.75 | 5.7696 | 0.12999 | 105 | 0.2 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Sand aggregate on metal lath - 3/4 in. | [5 empty] | From CEC Title24 2013
Shingles - Asbestos cement - lapped - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.1904 | 0.21001 | 120 | 0.24 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asbestos cement - lapped - 1/4 in. | [5 empty] | From CEC Title24 2013
Shingles - Asphalt roll siding - 1/4 in. | StandardOpaqueMaterial | VeryRough | 0.25 | 1.6704 | 0.14966 | 70 | 0.36 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Asphalt roll siding - 1/4 in. | [5 empty] | From CEC Title24 2013
Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | StandardOpaqueMaterial | MediumRough | 0.5 | 0.57 | 0.87719 | 22 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - 16 in. - 7 1/2 in. exposure - 1/2 in. | [5 empty] | From CEC Title24 2013
Shingles - Wood - plus insulated backer board Siding - 5/16 in. | StandardOpaqueMaterial | MediumRough | 0.31 | 0.2196 | 1.4117 | 22 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Shingles - Wood - plus insulated backer board Siding - 5/16 in. | [5 empty] | From CEC Title24 2013
Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 0.3396 | 1.4723 | 70 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Asphalt insulating siding - 1/2 in. bed - 1/2 in. | [5 empty] | From CEC Title24 2013
Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | StandardOpaqueMaterial | Rough | 0.75 | 0.7104 | 1.0557 | 22 | 0.28 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Siding - Wood - bevel - 10 in. - lapped - 3/4 in. | [5 empty] | From CEC Title24 2013
Simple Glazing | SimpleGlazing | [10 empty] | 1.23 | 0.61 | 0.25
SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.2435 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.0802 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - I Joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23952 | 27.1376 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.25356 | 32.5367 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.867 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - I Joist Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.2436 | 33.867 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.1842 | 35.2877 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.498 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - I Joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.16884 | 38.498 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.26628 | 38.4933 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2424 | 42.2855 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - I Joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25428 | 40.3099 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32364 | 20.084 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29772 | 21.8326 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - I Joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30636 | 21.2169 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.3144 | 26.2405 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.29376 | 28.0842 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - I Joist Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.30408 | 27.131 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23148 | 28.0802 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.19968 | 32.5521 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - I Joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2076 | 31.3102 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.315 | 32.5397 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.2961 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - I Joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.2961 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Floor | SIPS - No Crawl Space - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R14 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.39312 | 11.4469 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Double 2x Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R14 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35304 | 12.7464 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - I joist Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R14 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 4.14 | 11.5942 | 1.83 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R14 - Metal Spline - 48 in. | [5 empty] | From CEC Title24 2013
SIPS - R14 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.8515 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - OSB Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R14 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.35868 | 12.546 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R14 - Single 2x Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R18 - Double 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.3306 | 13.6116 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Double 2x Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R18 - I joist Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.29208 | 15.4067 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - I joist Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R18 - OSB Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.25968 | 17.329 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - OSB Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R18 - Single 2x Spline - 4 1/2 in. | StandardOpaqueMaterial | Smooth | 4.5 | 0.303 | 14.8515 | 9.89 | 0.31 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R18 - Single 2x Spline - 4 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.32496 | 20.0025 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3828 | 16.9801 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.30216 | 21.5118 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - I joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.33696 | 19.2901 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - I joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 3.0396 | 15.7916 | 1.83 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Metal Spline - 48 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28692 | 22.6544 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - OSB Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.28452 | 22.8455 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - OSB Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.3096 | 20.9948 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R22 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.35208 | 18.4617 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R22 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - Double 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.33612 | 25.2886 | 5.71 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Double 2x Spline - 8 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - Double 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.37992 | 21.7151 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Double 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - I joist Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.5618 | 5.71 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - I joist Spline - 8 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - I joist Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.32364 | 25.4913 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - I joist Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.4569 | 19.537 | 1.83 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Metal Spline - 48 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - OSB Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.2976 | 28.5618 | 5.71 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - OSB Spline - 8 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - OSB Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.27768 | 29.7105 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - OSB Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - Single 2x Spline - 8 1/2 in. | StandardOpaqueMaterial | Smooth | 8.5 | 0.3072 | 27.6693 | 5.71 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R28 - Single 2x Spline - 8 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R28 - Single 2x Spline - 8 1/4 in. | StandardOpaqueMaterial | Smooth | 8.25 | 0.34236 | 24.0974 | 5.85 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R28 - Single 2x Spline - 8 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.23484 | 27.6784 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - Double 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.29928 | 21.7188 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Double 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.5164 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - I joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - I joist Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.24768 | 26.2435 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - I joist Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.2058 | 31.5841 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - OSB Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - OSB Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.21876 | 29.7129 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - OSB Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.213 | 30.5164 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R33 - Single 2x Spline - 6 1/2 in. | StandardOpaqueMaterial | Smooth | 6.5 | 0.26232 | 24.7789 | 7.15 | 0.3 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R33 - Single 2x Spline - 6 1/2 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.31308 | 32.7392 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3792 | 27.0306 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2904 | 35.2961 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - I joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.32244 | 31.7889 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - I joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - Metal Spline - 48 in. | StandardOpaqueMaterial | Smooth | 48 | 2.2296 | 21.5285 | 1.83 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Metal Spline - 48 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27912 | 36.7226 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - OSB Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.27756 | 36.929 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - OSB Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.30168 | 33.9764 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R36 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.345 | 29.7101 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R36 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.32016 | 38.2621 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Double 2x Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - Double 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.35844 | 34.1759 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Double 2x Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.2802 | 43.7188 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - I joist Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - I joist Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.31848 | 38.464 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - I joist Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.267 | 45.8801 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - OSB Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - OSB Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.279 | 43.9068 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - OSB Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.29352 | 41.7348 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R44 - Single 2x Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R44 - Single 2x Spline - 12 1/4 in. | StandardOpaqueMaterial | Smooth | 12.25 | 0.34512 | 35.4949 | 4.27 | 0.28 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R44 - Single 2x Spline - 12 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.22344 | 45.8736 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - Double 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.3 | 34.1667 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Double 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.19044 | 53.8227 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - I joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - I joist Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.2334 | 43.916 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - I joist Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.17952 | 57.0967 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - OSB Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - OSB Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.21156 | 48.4496 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - OSB Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.20136 | 50.9039 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Roof | SIPS - R55 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
SIPS - R55 - Single 2x Spline - 10 1/4 in. | StandardOpaqueMaterial | Smooth | 10.25 | 0.25548 | 40.1206 | 4.9 | 0.29 | [20 empty] | CEC Title24-2013 | JA4-10 | SIPS Wall | SIPS - R55 - Single 2x Spline - 10 1/4 in. | [5 empty] | From CEC Title24 2013
Skylight_Frame_Width_0.000_in |  |  |  |  | 0 | [21 empty] | 0
Skylight_Frame_Width_0.334_in |  |  |  |  | 0.02 | [21 empty] | 4.004
Skylight_Frame_Width_0.430_in |  |  |  |  | 0.02 | [21 empty] | 5.157
Skylight_Frame_Width_0.709_in |  |  |  |  | 0.02 | [21 empty] | 8.504
Skylight_Frame_Width_2.339_in |  |  |  |  | 0.02 | [21 empty] | 28.07
Slate - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.045329 | 119.81 | 0.3 | [20 empty] | CEC Title24-2013 | CEC Doug | Roofing | Slate - 1/2 in. | [5 empty] | From CEC Title24 2013
Slate or tile - 1/2 in. | StandardOpaqueMaterial | VeryRough | 0.5 | 11.0304 | 0.045329 | 119.81 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Slate or tile - 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3204 | 10.9238 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3204 | 14.0449 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3204 | 12.4844 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3204 | 17.166 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3204 | 15.6055 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 5 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3204 | 20.2871 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3204 | 18.7266 | 4.6 | 0.34 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Cellulosic fiber - 4.6 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | MediumRough | 3.5 | 0.27 | 12.963 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | MediumRough | 4.5 | 0.27 | 16.6667 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | StandardOpaqueMaterial | MediumRough | 4 | 0.27 | 14.8148 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | MediumRough | 5.5 | 0.27 | 20.3704 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | StandardOpaqueMaterial | MediumRough | 5 | 0.27 | 18.5185 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 5 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | MediumRough | 6.5 | 0.27 | 24.0741 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | StandardOpaqueMaterial | MediumRough | 6 | 0.27 | 22.2222 | 3.9 | 0.23 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Glass fiber - 3.9 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.3 | 11.6667 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.3 | 15 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.3 | 13.3333 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.3 | 18.3333 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.3 | 16.6667 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 5 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.3 | 21.6667 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.3 | 20 | 0.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 0.5 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | StandardOpaqueMaterial | Rough | 3.5 | 0.20004 | 17.4965 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 3 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | StandardOpaqueMaterial | Rough | 4.5 | 0.20004 | 22.4955 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | StandardOpaqueMaterial | Rough | 4 | 0.20004 | 19.996 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 4 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | StandardOpaqueMaterial | Rough | 5.5 | 0.20004 | 27.4945 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | StandardOpaqueMaterial | Rough | 5 | 0.20004 | 24.995 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 5 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | StandardOpaqueMaterial | Rough | 6.5 | 0.20004 | 32.4935 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 1/2 in. | [5 empty] | From CEC Title24 2013
Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | StandardOpaqueMaterial | Rough | 6 | 0.20004 | 29.994 | 3 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Insulation Spray Applied | Spray applied - Polyurethane foam - 3.0 lb/ft3 - 6 in. | [5 empty] | From CEC Title24 2013
Std Wood 6 in. | StandardOpaqueMaterial | MediumSmooth | 5.9055 | 0.83202 | 7.0978 | 33.7111 | 0.289 | 0.9 | 0.7 | 0.7
Std Wood 6inch Furnishings | StandardOpaqueMaterial | MediumSmooth | 5.91 | 0.83257 |  | 33.71 | 0.29 | 0.9 | 0.7 | 0.7
Steel Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame Wall Insulation R-1.02 IP | StandardOpaqueMaterial | MediumRough | 0.34789 | 0.33974 | 1.024 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Steel Frame/Cavity | StandardOpaqueMaterial | MediumRough | 3.5 | 0.58322 | 6.0012 | 40.04 | 0.11992 | 0.9 | 0.7 | 0.7
Stone - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.079974 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Stone - 1 in. | [5 empty] | From CEC Title24 2013
Straw Bale - Int and Ext Stucco - 18 in. | StandardOpaqueMaterial | Smooth | 19.5 | 0.6504 | 29.9815 | 12.95 | 0.11 | [20 empty] | CEC Title24-2013 | JA4-10 | Straw Bale Wall | Straw Bale - Int and Ext Stucco - 18 in. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.81 | 2.8025 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - No Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.5304 | 6.1652 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R10 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.64764 | 6.902 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R15 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.7704 | 7.3598 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R20 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.8904 | 7.7156 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R25 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.02 | 7.9118 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R30 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.39 | 4.6923 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R4 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Double glass with no low e coatings - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.4596 | 5.5483 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Double glass with no low e coatings - R7 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | StandardOpaqueMaterial | Smooth | 2.52 | 1.2804 | 1.9681 | 41.9 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - No Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.52 | 0.5904 | 5.9621 | 30.2 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R10 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.72 | 0.6996 | 6.7467 | 22.79 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R15 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.92 | 0.81324 | 7.2795 | 18.37 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R20 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | StandardOpaqueMaterial | Smooth | 7.12 | 0.93372 | 7.6254 | 15.45 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R25 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.32 | 1.05 | 7.9238 | 13.37 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R30 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | StandardOpaqueMaterial | Smooth | 2.08 | 0.48624 | 4.2777 | 50.36 | 0.25 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R4 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.8 | 0.5304 | 5.279 | 37.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Single glass pane. stone. or metal pane - R7 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - No Ins. | StandardOpaqueMaterial | Smooth | 2.27 | 0.6504 | 3.4902 | 29.09 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - No Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R10 Ins. | StandardOpaqueMaterial | Smooth | 3.27 | 0.51 | 6.4118 | 20.44 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R10 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R15 Ins. | StandardOpaqueMaterial | Smooth | 4.47 | 0.63636 | 7.0243 | 15.23 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R15 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R20 Ins. | StandardOpaqueMaterial | Smooth | 5.67 | 0.76476 | 7.4141 | 12.22 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R20 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R25 Ins. | StandardOpaqueMaterial | Smooth | 6.87 | 0.88404 | 7.7711 | 10.26 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R25 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R30 Ins. | StandardOpaqueMaterial | Smooth | 8.07 | 1.0104 | 7.9869 | 8.88 | 0.27 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R30 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R4 Ins. | StandardOpaqueMaterial | Smooth | 1.83 | 0.36 | 5.0833 | 35.69 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R4 Ins. | [5 empty] | From CEC Title24 2013
Structural Glazing - Triple or low e glass - R7 Ins. | StandardOpaqueMaterial | Smooth | 2.55 | 0.43836 | 5.8171 | 25.92 | 0.26 | [20 empty] | CEC Title24-2013 | JA4-10 | Spandrel Panels Curtain Walls | Structural Glazing - Triple or low e glass - R7 Ins. | [5 empty] | From CEC Title24 2013
Stucco - 3/8 in. | StandardOpaqueMaterial | Smooth | 0.38 | 5.0004 | 0.075994 | 115.81 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 3/8 in. | [5 empty] | From CEC Title24 2013
Stucco - 7/8 in. | StandardOpaqueMaterial | Smooth | 0.88 | 4.86 | 0.18107 | 115.81 | 0.2 | [20 empty] | CEC Title24-2013 | CEC Doug | Plastering Materials | Stucco - 7/8 in. | [5 empty] | From CEC Title24 2013
Stucco - 7/8 in. CBES | StandardOpaqueMaterial | MediumRough | 0.88 | 4.8567 |  | 115.81 | 0.2 | 0.9 | 0.7 | 0.8
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.0064 | 1.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | From CEC Title24 2013
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.0064 | 1.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Masonry Materials | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | From CEC Title24 2013
Synthetic Stucco - EIFS finish - 1 in. | StandardOpaqueMaterial | Smooth | 1 | 0.2496 | 4.0064 | 1.5 | 0.35 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Synthetic Stucco - EIFS finish - 1 in. | [5 empty] | From CEC Title24 2013
Terrazzo - 1 in. | StandardOpaqueMaterial | Rough | 1 | 12.5004 | 0.079997 | 160 | 0.19 | [20 empty] | CEC Title24-2013 | AEC | Finish Materials | Terrazzo - 1 in. | [5 empty] | From CEC Title24 2013
Terrazzo - 1 in. | StandardOpaqueMaterial | MediumRough | 1 | 12.504 | 0.079974 | 139.78 | 0.22 | [20 empty] | CEC Title24-2013 | CEC Doug | Masonry Materials | Terrazzo - 1 in. | [5 empty] | From CEC Title24 2013
Test | Test | Test | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | [17 empty] | CEC Title24-2013 | AEC | Woods | Wood siding - 1/2 in. | [5 empty] | From CEC Title24 2013
Theoretical Glass [167] | StandardGlazing |  | 0.11811 | 14.6109 | 0.068442 | [9 empty] | SpectralAverage | 0.2374 | 0.7126 | 0.7126 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.985 | 0.985 | 1 | FALSE
Theoretical Glass [197] | StandardGlazing |  | 0.11811 | 0.28774 | 3.4754 | [9 empty] | SpectralAverage | 0.2349 | 0.7151 | 0.7151 | 0.2512 | 0.6988 | 0.6988 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [202] | StandardGlazing |  | 0.11811 | 0.13312 | 7.5119 | [9 empty] | SpectralAverage | 0.2325 | 0.7175 | 0.7175 | 0.3192 | 0.6308 | 0.6308 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [207] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3311 | 0.6189 | 0.6189 | 0.44 | 0.51 | 0.51 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [216] | StandardGlazing |  | 0.11811 | 0.092215 | 10.8442 | [9 empty] | SpectralAverage | 0.3801 | 0.5699 | 0.5699 | 0.5079 | 0.4421 | 0.4421 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass [221] | StandardGlazing |  | 0.11811 | 0.061708 | 16.2054 | [9 empty] | SpectralAverage | 0.4296 | 0.5204 | 0.5204 | 0.4503 | 0.4997 | 0.4997 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass 297 | StandardGlazing |  | 0.11811 | 0.071804 | 13.9269 | [9 empty] | SpectralAverage | 0.37504 | 0.57496 | 0.57496 | 0.5297 | 0.4203 | 0.4203 | 0 | 0.9 | 0.9 | 1 | FALSE
Theoretical Glass 347 | StandardGlazing |  | 0.11811 | 0.071817 | 13.9243 | [9 empty] | SpectralAverage | 0.31586 | 0.63414 | 0.63414 | 0.47991 | 0.47009 | 0.47009 | 0 | 0.9 | 0.9 | 1 | FALSE
Tile Gap - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.6612 | 1.1343 | 70 | 0.24 | [20 empty] | CEC Title24-2013 | CEC Bruce | Roofing | Tile Gap - 3/4 in. | [5 empty] | From CEC Title24 2013
Typical Air Wall | MasslessOpaqueMaterial |  |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
Typical Carpet Pad | MasslessOpaqueMaterial | VeryRough |  |  | 1.2292 |  |  | 0.9 | 0.7 | 0.8
Typical Insulation | MasslessOpaqueMaterial | MediumSmooth |  | 6.2401 | 0.16025 | 0.0437 | 0.00016719 | 0.9 | 0.7 | 0.7
U 0.11 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.11 | 0.34 | 0.374
U 0.11 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.11 | 0.38 | 0.418
U 0.12 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.12 | 0.34 | 0.374
U 0.12 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.12 | 0.38 | 0.418
U 0.13 SHGC 0.32 Simple Glazing | SimpleGlazing | [10 empty] | 0.13 | 0.32 | 0.352
U 0.13 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.13 | 0.38 | 0.418
U 0.14 SHGC 0.31 Simple Glazing | SimpleGlazing | [10 empty] | 0.14 | 0.31 | 0.341
U 0.14 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.14 | 0.34 | 0.374
U 0.14 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.14 | 0.36 | 0.396
U 0.14 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.14 | 0.38 | 0.418
U 0.15 SHGC 0.31 Simple Glazing | SimpleGlazing | [10 empty] | 0.15 | 0.31 | 0.341
U 0.15 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.15 | 0.34 | 0.374
U 0.17 SHGC 0.31 Simple Glazing | SimpleGlazing | [10 empty] | 0.17 | 0.31 | 0.341
U 0.17 SHGC 0.32 Simple Glazing | SimpleGlazing | [10 empty] | 0.17 | 0.32 | 0.352
U 0.17 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.17 | 0.36 | 0.396
U 0.18 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.18 | 0.22 | 0.242
U 0.18 SHGC 0.24 Simple Glazing | SimpleGlazing | [10 empty] | 0.18 | 0.24 | 0.264
U 0.20 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.2 | 0.19 | 0.209
U 0.20 SHGC 0.20 Simple Glazing | SimpleGlazing | [10 empty] | 0.2 | 0.2 | 0.22
U 0.20 SHGC 0.21 Simple Glazing | SimpleGlazing | [10 empty] | 0.2 | 0.21 | 0.231
U 0.20 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.2 | 0.22 | 0.242
U 0.23 SHGC 0.31 Simple Glazing | SimpleGlazing | [10 empty] | 0.23 | 0.31 | 0.341
U 0.23 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.23 | 0.34 | 0.374
U 0.25 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.25 | 0.22 | 0.242
U 0.25 SHGC 0.24 Simple Glazing | SimpleGlazing | [10 empty] | 0.25 | 0.24 | 0.264
U 0.26 SHGC 0.40 Simple Glazing | SimpleGlazing | [10 empty] | 0.26 | 0.4 | 0.44
U 0.29 SHGC 0.40 Simple Glazing | SimpleGlazing | [10 empty] | 0.29 | 0.4 | 0.44
U 0.32 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.32 | 0.36 | 0.396
U 0.34 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.34 | 0.38 | 0.418
U 0.35 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.35 | 0.22 | 0.242
U 0.35 SHGC 0.24 Simple Glazing | SimpleGlazing | [10 empty] | 0.35 | 0.24 | 0.264
U 0.36 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.36 | 0.36 | 0.396
U 0.36 SHGC 0.38 Simple Glazing | SimpleGlazing | [10 empty] | 0.36 | 0.38 | 0.418
U 0.42 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 0.42 | 0.25 | 0.275
U 0.42 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 0.42 | 0.34 | 0.374
U 0.45 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 0.45 | 0.25 | 0.275
U 0.45 SHGC 0.33 Simple Glazing | SimpleGlazing | [10 empty] | 0.45 | 0.33 | 0.363
U 0.47 SHGC 0.33 Simple Glazing | SimpleGlazing | [10 empty] | 0.47 | 0.33 | 0.363
U 0.48 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.48 | 0.19 | 0.209
U 0.48 SHGC 0.21 Simple Glazing | SimpleGlazing | [10 empty] | 0.48 | 0.21 | 0.231
U 0.48 SHGC 0.20 Simple Glazing | SimpleGlazing | [10 empty] | 0.48 | 0.2 | 0.22
U 0.48 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.48 | 0.22 | 0.242
U 0.50 SHGC 0.22 Simple Glazing | SimpleGlazing | [10 empty] | 0.5 | 0.22 | 0.242
U 0.50 SHGC 0.23 Simple Glazing | SimpleGlazing | [10 empty] | 0.5 | 0.23 | 0.253
U 0.52 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.39 | 0.31
U 0.52 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.49 | 0.41
U 0.52 SHGC 0.615 Simple Glazing | SimpleGlazing | [10 empty] | 0.52 | 0.615 | 0.41
U 0.54 SHGC 0.23 Simple Glazing | SimpleGlazing | [10 empty] | 0.54 | 0.23 | 0.253
U 0.58 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.58 | 0.19 | 0.15
U 0.58 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.58 | 0.36 | 0.25
U 0.59 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.59 | 0.36 | 0.27
U 0.59 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.59 | 0.39 | 0.31
U 0.60 SHGC 0.23 Simple Glazing | SimpleGlazing | [10 empty] | 0.6 | 0.23 | 0.253
U 0.61 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 0.61 | 0.77 | 0.6
U 0.62 SHGC 0.20 Simple Glazing | SimpleGlazing | [10 empty] | 0.62 | 0.2 | 0.22
U 0.62 SHGC 0.21 Simple Glazing | SimpleGlazing | [10 empty] | 0.62 | 0.21 | 0.231
U 0.62 SHGC 0.41 Simple Glazing | SimpleGlazing | 1.22 | 0.54 | 0.38 | [7 empty] | 0.62 | 0.41 | 0.32
U 0.65 SHGC 0.35 Simple Glazing | SimpleGlazing | [10 empty] | 0.65 | 0.35 | 0.25
U 0.69 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.19 | 0.15
U 0.69 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.36 | 0.23
U 0.69 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.39 | 0.23
U 0.69 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.49 | 0.38
U 0.69 SHGC 0.64 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.64 | 0.55
U 0.69 SHGC 0.68 Simple Glazing | SimpleGlazing | [10 empty] | 0.69 | 0.68 | 0.55
U 0.72 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.25 | 0.13
U 0.72 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.36 | 0.23
U 0.72 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 0.72 | 0.39 | 0.23
U 0.74 SHGC 0.55 Simple Glazing | SimpleGlazing | [10 empty] | 0.74 | 0.55 | 0.4
U 0.74 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.74 | 0.65 | 0.55
U 0.75 SHGC 0.35 Simple Glazing | SimpleGlazing | [10 empty] | 0.75 | 0.35 | 0.23
U 0.81 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.81 | 0.65 | 0.55
U 0.85 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 0.85 | 0.65 | 0.55
U 0.87 SHGC 0.58 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.58 | 0.55
U 0.87 SHGC 0.71 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.71 | 0.6
U 0.87 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 0.87 | 0.77 | 0.6
U 0.98 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 0.98 | 0.19 | 0.15
U 0.98 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 0.98 | 0.36 | 0.25
U 1.10 SHGC 0.62 Simple Glazing | SimpleGlazing | [10 empty] | 1.1 | 0.62 | 0.55
U 1.10 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 1.1 | 0.77 | 0.6
U 1.15 SHGC 0.77 Simple Glazing | SimpleGlazing | [10 empty] | 1.15 | 0.77 | 0.6
U 1.17 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.19 | 0.15
U 1.17 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.36 | 0.23
U 1.17 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.39 | 0.23
U 1.17 SHGC 0.49 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.49 | 0.38
U 1.17 SHGC 0.64 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.64 | 0.55
U 1.17 SHGC 0.68 Simple Glazing | SimpleGlazing | [10 empty] | 1.17 | 0.68 | 0.55
U 1.22 SHGC 0.25 Simple Glazing | SimpleGlazing | [10 empty] | 1.22 | 0.25 | 0.11
U 1.22 SHGC 0.54 Simple Glazing | SimpleGlazing | [10 empty] | 1.22 | 0.54 | 0.38
U 1.30 SHGC 0.27 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.27 | 0.25
U 1.30 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.34 | 0.25
U 1.30 SHGC 0.62 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.62 | 0.55
U 1.30 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 1.3 | 0.65 | 0.55
U 1.36 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.19 | 0.15
U 1.36 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.36 | 0.23
U 1.36 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.39 | 0.23
U 1.36 SHGC 0.61 Simple Glazing | SimpleGlazing | [10 empty] | 1.36 | 0.61 | 0.23
U 1.70 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.7 | 0.36 | 0.23
U 1.80 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.8 | 0.36 | 0.23
U 1.90 SHGC 0.27 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.27 | 0.25
U 1.90 SHGC 0.34 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.34 | 0.25
U 1.90 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.39 | 0.25
U 1.90 SHGC 0.65 Simple Glazing | SimpleGlazing | [10 empty] | 1.9 | 0.65 | 0.25
U 1.98 SHGC 0.16 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.16 | 0.15
U 1.98 SHGC 0.19 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.19 | 0.15
U 1.98 SHGC 0.36 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.36 | 0.25
U 1.98 SHGC 0.39 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.39 | 0.25
U 1.98 SHGC 0.61 Simple Glazing | SimpleGlazing | [10 empty] | 1.98 | 0.61 | 0.25
U0.47_SHGC_0.49_SimpleGlazing_Window_05 | SimpleGlazing | [9 empty] | Air | 0.47 | 0.49 | 0.81
U0.47_SHGC0.46_SimpleGlazing_Window_07 | SimpleGlazing | [9 empty] | Air | 0.47 | 0.46 | 0.81
U0.47_SHGC0.47_SimpleGlazing_Window_06 | SimpleGlazing | [9 empty] | Air | 0.47 | 0.47 | 0.81
U0.47_SHGC0.47_SimpleGlazing_Window_11 | SimpleGlazing | [9 empty] | Air | 0.47 | 0.47 | 0.81
U0.47_SHGC0.5_SimpleGlazing_Window_03 | SimpleGlazing | [9 empty] | Air | 0.47 | 0.5 | 0.81
U0.77_SHGC_0.77_SimpleGlazing_Window_02 | SimpleGlazing | [9 empty] | Air | 0.77 | 0.77 | 0.81
U0.77_SHGC0.5_SimpleGlazing_Window_09 | SimpleGlazing | [9 empty] | Air | 0.77 | 0.5 | 0.81
U0.77_SHGC0.61_SimpleGlazing_Window_08 | SimpleGlazing | [9 empty] | Air | 0.77 | 0.61 | 0.81
U0.77_SHGC0.62_SimpleGlazing_Window_04 | SimpleGlazing | [9 empty] | Air | 0.77 | 0.62 | 0.81
U1.23_SHGC0.5_SimpleGlazing_Window_12 | SimpleGlazing | [9 empty] | Air | 1.23 | 0.5 | 0.81
U1.23_SHGC0.82_SimpleGlazing_Window_01 | SimpleGlazing | [9 empty] | Air | 1.23 | 0.82 | 0.81
U1.23_SHGC0.82_SimpleGlazing_Window_10 | SimpleGlazing | [9 empty] | Air | 1.23 | 0.62 | 0.81
Vapor permeable felt - 1/8 in. | StandardOpaqueMaterial | Rough | 0.13 | 2.0796 | 0.062512 | 22 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor permeable felt - 1/8 in. | [5 empty] | From CEC Title24 2013
Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | StandardOpaqueMaterial | Rough | 0.25 | 2.0796 | 0.12022 | 22 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - 2 layers of mopped 15 lb felt - 1/4 in. | [5 empty] | From CEC Title24 2013
Vapor seal - plastic film - 1/16 in. | StandardOpaqueMaterial | Rough | 0.63 | 62.4996 | 0.01008 | 30 | 0.3 | [20 empty] | CEC Title24-2013 | AEC | Building Membrane | Vapor seal - plastic film - 1/16 in. | [5 empty] | From CEC Title24 2013
Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | StandardOpaqueMaterial | Smooth | 0.5 | 1.7004 | 0.29405 | 45 | 0.32 | [20 empty] | CEC Title24-2013 | AEC | Plastering Materials | Vermiculite aggregate - 45 lb/ft3 - 1/2 in. | [5 empty] | From CEC Title24 2013
W_m1_R15 | StandardOpaqueMaterial | Smooth | 2.394 | 0.15963 | 15 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W_m2_R19 | StandardOpaqueMaterial | Smooth | 3.0324 | 0.15963 | 19 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W_m3_R21 | StandardOpaqueMaterial | Smooth | 3.3516 | 0.15963 | 21 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W_T24_2013_R13.99 | StandardOpaqueMaterial | Smooth | 2.2328 | 0.15963 | 13.99 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W1_R8.60 | StandardOpaqueMaterial | Smooth | 1.3725 | 0.15963 | 8.6 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W2_R11.13 | StandardOpaqueMaterial | Smooth | 1.7763 | 0.15963 | 11.13 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W3_R11.36 | StandardOpaqueMaterial | Smooth | 1.8131 | 0.15963 | 11.36 | 1 | 0.27 | 0.9 | 0.7 | 0.8
W4_R12.62 | StandardOpaqueMaterial | Smooth | 2.0141 | 0.15963 | 12.62 | 1 | 0.27 | 0.9 | 0.7 | 0.8
Wall Insulation [31] | StandardOpaqueMaterial | MediumRough | 1.3268 | 0.29953 | 4.4296 | 5.6809 | 0.19991 | 0.9 | 0.5 | 0.5
Wood - 1 in. | StandardOpaqueMaterial | MediumSmooth | 1 | 1.0404 | 0.96117 | 37.94 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1 in. | [5 empty] | From CEC Title24 2013
Wood - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 1.0404 | 0.48058 | 37.94 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Wood - 1/2 in. | [5 empty] | From CEC Title24 2013
Wood - 2 in. | StandardOpaqueMaterial | MediumSmooth | 2 | 1.0404 | 1.9223 | 37.94 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Wood - 2 in. | [5 empty] | From CEC Title24 2013
Wood - 4 in. | StandardOpaqueMaterial | MediumSmooth | 4 | 1.0404 | 3.8447 | 37.94 | 0.39 | [20 empty] | CEC Title24-2013 | AEC | Woods | Wood - 4 in. | [5 empty] | From CEC Title24 2013
Wood Frame NonRes Wall Insulation-0.73 | StandardOpaqueMaterial | MediumRough | 0.79836 | 0.33974 | 2.3499 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Frame Wall Insulation R-1.61 IP | StandardOpaqueMaterial | MediumRough | 0.54621 | 0.33974 | 1.6077 | 16.5434 | 0.19987 | 0.9 | 0.7 | 0.7
Wood Framed Attic Floor - 16inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.783 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.4765 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.1561 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5953 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 28.8982 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 31.873 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.1444 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 38.5802 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 9_25In | 2x10 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0136 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.7862 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.7471 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2917 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.045 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2328 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 33.9752 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 36.5684 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 41.7037 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 11_25In | 2x12 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 13.9437 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.333 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4178 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.9895 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 19.0316 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 20.278 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 21.1742 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 22.7998 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 3_5In | 2x4 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.8706 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 18.394 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 20.6759 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 23.7814 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 25.7599 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 27.2236 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 29.9711 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 5_5In | 2x6 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.4438 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.0246 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 20.0271 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.7622 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.584 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.0808 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 30.96 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 16inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 34.5633 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof16inOC | 7_25In | 2x8 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.8472 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.6291 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.6705 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.2568 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 31.1355 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 34.7459 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 37.5607 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x10 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 43.2077 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 9_25In | 2x10 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 11.0095 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.8496 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 18.1053 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 19.7743 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.594 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.9964 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 36.4678 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 39.581 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x12 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 45.903 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 11_25In | 2x12 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 15.5068 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 16.0065 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 17.421 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 19.5305 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 22.3835 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 24.1906 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 25.5222 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x4 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 28.0096 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 3_5In | 2x4 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.1394 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 19.9777 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 22.802 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 26.7885 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 29.4185 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 31.4116 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x6 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 35.2661 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 5_5In | 2x6 | 60 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.6047 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 11 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 12.3015 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 13 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.298 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.5383 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 29.2172 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 38 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R44 ins. | MasslessOpaqueMaterial |  |  |  | 32.3739 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 44 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R49 ins. | MasslessOpaqueMaterial |  |  |  | 34.804 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 49 | From CEC Title24 2013
Wood Framed Attic Floor - 24inOC - 2x8 - R60 ins. | MasslessOpaqueMaterial |  |  |  | 39.5997 | [22 empty] | CEC Title24-2013 |  | Wood Framed Attic Floor |  | Wood | Roof24inOC | 7_25In | 2x8 | 60 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Floor - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 18.2344 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor16inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Floor - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2214 | [22 empty] | CEC Title24-2013 |  | Wood Framed Floor |  | Wood | Floor24inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 19.2942 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 22 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 21.3129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 24.4379 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.6551 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 30.6158 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 11_25In | 2x14 | 38 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.0352 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.1946 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 11.2537 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.1185 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.9817 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.416 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.7607 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 15 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 15.2129 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 16.3338 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.313 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 16inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.6089 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof16inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x10 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 20.0334 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 22 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x10 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 22.2995 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 25 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x10 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 25.8772 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 9_25In | 2x10 | 30 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x12 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 26.8204 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 30 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x12 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x12 | 38 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x14 - R38 ins. | MasslessOpaqueMaterial |  |  |  | 32.5111 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 11_25In | 2x14 | 38 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 9.5468 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 10.9003 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 12.1652 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x4 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 14.4614 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 3_5In | 2x4 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x6 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 10.2668 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 11 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x6 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 11.8491 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 13 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x6 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 13.359 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 15 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 16.1804 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 17.5004 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 17.0358 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Rafter Roof - 24inOC - 2x8 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 18.5054 | [22 empty] | CEC Title24-2013 |  | Wood Framed Rafter Roof |  | Wood | Roof24inOC | 7_25In | 2x8 | 21 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.126 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 7.7016 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.1867 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 11.7113 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.2507 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 12.4993 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.4581 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 14.5092 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 15.4247 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Wall - 16inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 16.7137 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall16inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R11 ins. | MasslessOpaqueMaterial |  |  |  | 7.4404 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.0311 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R13 ins. | MasslessOpaqueMaterial |  |  |  | 8.0977 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 8.8567 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R15 ins. | MasslessOpaqueMaterial |  |  |  | 8.6586 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 9.579 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 12.2765 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.3502 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R21 ins. | MasslessOpaqueMaterial |  |  |  | 12.8954 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.1353 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 13.1824 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.5036 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R19 ins. | MasslessOpaqueMaterial |  |  |  | 13.9462 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 14.8435 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R22 ins. | MasslessOpaqueMaterial |  |  |  | 15.1272 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 16.2834 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R25 ins. | MasslessOpaqueMaterial |  |  |  | 16.1678 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.5793 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R30 ins. | MasslessOpaqueMaterial |  |  |  | 17.6518 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | Wall24inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood Framed Wall - 24inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.4735 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS24inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x4 - R11 ins. AWS | MasslessOpaqueMaterial |  |  |  | 10.1197 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 11 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x4 - R13 ins. AWS | MasslessOpaqueMaterial |  |  |  | 11.711 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 13 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x4 - R15 ins. AWS | MasslessOpaqueMaterial |  |  |  | 13.2373 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 3_5In | 2x4 | 15 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x6 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.2794 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 19 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x6 - R21 ins. AWS | MasslessOpaqueMaterial |  |  |  | 18.8464 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 21 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x6 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 19.6146 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 5_5In | 2x6 | 22 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x8 - R19 ins. AWS | MasslessOpaqueMaterial |  |  |  | 17.8255 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 19 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x8 - R22 ins. AWS | MasslessOpaqueMaterial |  |  |  | 20.3213 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 22 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x8 - R25 ins. AWS | MasslessOpaqueMaterial |  |  |  | 22.7412 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 25 | From CEC Title24 2013
Wood Framed Wall - 48inOC - 2x8 - R30 ins. AWS | MasslessOpaqueMaterial |  |  |  | 26.6149 | [22 empty] | CEC Title24-2013 |  | Wood Framed Wall |  | Wood | WallAWS48inOC | 7_25In | 2x8 | 30 | From CEC Title24 2013
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.90318 | 36.94 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - 3/4 in. | [5 empty] | From CEC Title24 2013
Wood shingles - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8304 | 0.90318 | 36.94 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - 3/4 in. | [5 empty] | From CEC Title24 2013
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.93703 | 22 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Bldg Board and Siding | Wood shingles - plain and plastic film faced - 3/4 in. | [5 empty] | From CEC Title24 2013
Wood shingles - plain and plastic film faced - 3/4 in. | StandardOpaqueMaterial | VeryRough | 0.75 | 0.8004 | 0.93703 | 22 | 0.31 | [20 empty] | CEC Title24-2013 | AEC | Roofing | Wood shingles - plain and plastic film faced - 3/4 in. | [5 empty] | From CEC Title24 2013
Wood Siding | StandardOpaqueMaterial | MediumSmooth | 0.3937 | 0.76268 | 0.51621 | 33.9995 | 0.289 | 0.9 | 0.78 | 0.78
Wood siding - 1/2 in. | StandardOpaqueMaterial | MediumSmooth | 0.5 | 0.6204 | 0.80593 | 36.94 | 0.28 | [20 empty] | CEC Title24-2013 | AEC | Woods | Wood siding - 1/2 in. | [5 empty] | From CEC Title24 2013

## Constructions
[5 empty] | Outside |  |  |  | Inside
Name | Intended Surface Type | Standards Construction Type | Insulation Layer | Skylight Framing | Material 1 | Material 2 | Material 3 | Material 4 | Material 5 | Material 6
Typical Attic Floor | AtticFloor | WoodFramed | Typical Insulation |  | 1/2IN Gypsum | Typical Insulation | 1/2IN Gypsum
Typical Wood Joist Attic Floor | AtticFloor | WoodFramed | Typical Insulation |  | 5/8 in. Gypsum Board | Typical Insulation
Typical Wood Joist Attic Floor Ceiling | AtticFloor | WoodFramed |  |  | Typical Insulation | 5/8 in. Gypsum Board
Typical Uninsulated Metal Roof Attic Roof | AtticRoof | WoodFramed |  |  | Roof Membrane | Metal Decking
Typical Uninsulated Wood Joist Attic Roof | AtticRoof | WoodFramed |  |  | Asphalt Shingles | 5/8 in. Plywood
Typical Attic Soffit | AtticWall |  |  |  | 5/8 in. Plywood
Typical Insulated Metal Door | ExteriorDoor |  | Typical Insulation |  | F08 Metal surface | Typical Insulation
Typical Overhead Door | ExteriorDoor | RollUp | Typical Insulation |  | Typical Insulation
Typical Uninsulated Swinging Door | ExteriorDoor | Swinging | Typical Insulation |  | Typical Insulation
Adiabatic ExteriorFloor | ExteriorFloor | Mass |  |  | Adiabatic Material
Typical Carpeted 4in Slab Floor | ExteriorFloor |  |  |  | MAT-CC05 4 HW CONCRETE | Typical Carpet Pad
Typical Insulated Carpeted 4in Slab Floor | ExteriorFloor |  | Typical Insulation |  | Typical Insulation | MAT-CC05 4 HW CONCRETE | Typical Carpet Pad
Typical Insulated Exterior Mass Floor | ExteriorFloor | Mass | Typical Insulation |  | Typical Insulation | 4 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Insulated Exterior Mass Floor Ceiling | ExteriorFloor | Mass | Typical Insulation |  | Typical Carpet Pad | 4 in. Normalweight Concrete Floor | Typical Insulation
Typical Insulated Steel Framed Exterior Floor | ExteriorFloor | SteelFramed | Typical Insulation |  | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board | Typical Carpet Pad
Typical Insulated Wood Framed Exterior Floor | ExteriorFloor | WoodFramed | Typical Insulation |  | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board | Typical Carpet Pad
Typical Uncarpeted 4in Slab Floor | ExteriorFloor |  |  |  | MAT-CC05 4 HW CONCRETE
Adiabatic Roof | ExteriorRoof | Attic and Other |  |  | Adiabatic Material
Metal roofR_R30 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R_R30
Metal roofR_R38 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R_R38
Metal roofR_T24_2013_24.86 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R_T24_2013_24.86
Metal roofR1_R14.20 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R1_R14.20
Metal roofR2_R12.90 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R2_R12.90
Metal roofR3_R17.74 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R3_R17.74
Metal roofR4_R20.28 | ExteriorRoof |  | Typical Insulation |  | Metal Standing Seam - 1/16 in. CBES | R4_R20.28
Typical Built Up Roof | ExteriorRoof | IEAD | Typical Insulation |  | Built-up Roofing | Typical Insulation | Metal Surface
Typical Built Up Roof - Highly Reflective | ExteriorRoof | IEAD | Typical Insulation |  | Built-up Roofing - Highly Reflective | Typical Insulation | Metal Surface
Typical IEAD Roof | ExteriorRoof | IEAD | Typical Insulation |  | Roof Membrane | Typical Insulation | Metal Roof Surface
Typical IEAD Roof - Highly Reflective | ExteriorRoof | IEAD | Typical Insulation |  | Roof Membrane - Highly Reflective | Typical Insulation | Metal Roof Surface
Typical Insulated Metal Building Roof | ExteriorRoof | Metal Building | Typical Insulation |  | Metal Roof Surface | Typical Insulation
Typical Insulated Metal Building Roof - Highly Reflective | ExteriorRoof | Metal Building | Typical Insulation |  | Metal Roof Surface - Highly Reflective | Typical Insulation
Typical Uninsulated Metal Building Roof | ExteriorRoof | Metal Building |  |  | Metal Roofing
Typical Uninsulated Metal Building Roof - Highly Reflective | ExteriorRoof | Metal Building |  |  | Metal Roofing - Highly Reflective
Adiabatic Wall | ExteriorWall | Mass |  |  | Adiabatic Material
Metal framed wallsW_m1_R15 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W_m1_R15 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW_m2_R19 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W_m2_R19 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW_m3_R21 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W_m3_R21 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW_T24_2013_R13.99 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W_T24_2013_R13.99 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW1_R8.60 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W1_R8.60 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW2_R11.13 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W2_R11.13 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW3_R11.36 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W3_R11.36 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Metal framed wallsW4_R12.62 | ExteriorWall |  | Typical Insulation |  | Stucco - 7/8 in. CBES | W4_R12.62 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 1/2 in. CBES
Typical Insulated Exterior Mass Wall | ExteriorWall | Mass | Typical Insulation |  | 1IN Stucco | 8IN CONCRETE HW RefBldg | Typical Insulation | 1/2IN Gypsum
Typical Insulated Metal Building Wall | ExteriorWall | Metal Building | Typical Insulation |  | Metal Siding | Typical Insulation | 1/2IN Gypsum
Typical Insulated Steel Framed Exterior Wall | ExteriorWall | SteelFramed | Typical Insulation |  | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board
Typical Insulated Wood Framed Exterior Wall | ExteriorWall | WoodFramed | Typical Insulation |  | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | 5/8 in. Gypsum Board
Typical Uninsulated Exterior Mass Wall | ExteriorWall | Mass |  |  | 1IN Stucco | 8IN CONCRETE HW RefBldg | 1/2IN Gypsum
Typical Uninsulated Metal Building Wall | ExteriorWall | Metal Building |  |  | Metal Siding | 1/2IN Gypsum
Typical Uninsulated Steel Framed Exterior Wall | ExteriorWall | SteelFramed |  |  | Wood Siding | 1/2IN Gypsum
WoodWallU110 | ExteriorWall |  |  |  | Plywood - 5/8 in. | Compliance Insulation R6.46 | Air - Metal Wall Framing - 16 or 24 in. OC | Gypsum Board - 3/8 in.
ASHRAE 189.1-2009 ExtWindow ClimateZone 1 | ExteriorWindow |  |  |  | Theoretical Glass [167]
ASHRAE 189.1-2009 ExtWindow ClimateZone 2 | ExteriorWindow |  |  |  | Theoretical Glass [197]
ASHRAE 189.1-2009 ExtWindow ClimateZone 3 | ExteriorWindow |  |  |  | Theoretical Glass [202]
ASHRAE 189.1-2009 ExtWindow ClimateZone 4-5 | ExteriorWindow |  |  |  | Theoretical Glass [207]
ASHRAE 189.1-2009 ExtWindow ClimateZone 6 | ExteriorWindow |  |  |  | Theoretical Glass [216]
ASHRAE 189.1-2009 ExtWindow ClimateZone 7-8 | ExteriorWindow |  |  |  | Theoretical Glass [221]
ASHRAE 189.1-2009 ExtWindow ClimateZone alt-res 4-5 | ExteriorWindow |  |  |  | Theoretical Glass [216]
U 0.11 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.11 SHGC 0.34 Simple Glazing
U 0.11 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.11 SHGC 0.38 Simple Glazing
U 0.12 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.12 SHGC 0.34 Simple Glazing
U 0.12 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.12 SHGC 0.38 Simple Glazing
U 0.13 SHGC 0.32 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.13 SHGC 0.32 Simple Glazing
U 0.13 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.13 SHGC 0.38 Simple Glazing
U 0.14 SHGC 0.31 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.14 SHGC 0.31 Simple Glazing
U 0.14 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.14 SHGC 0.34 Simple Glazing
U 0.14 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.14 SHGC 0.36 Simple Glazing
U 0.14 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.14 SHGC 0.38 Simple Glazing
U 0.15 SHGC 0.31 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.15 SHGC 0.31 Simple Glazing
U 0.15 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.15 SHGC 0.34 Simple Glazing
U 0.17 SHGC 0.31 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.17 SHGC 0.31 Simple Glazing
U 0.17 SHGC 0.32 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.17 SHGC 0.32 Simple Glazing
U 0.17 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.17 SHGC 0.36 Simple Glazing
U 0.18 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.18 SHGC 0.22 Simple Glazing
U 0.18 SHGC 0.24 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.18 SHGC 0.24 Simple Glazing
U 0.19 SHGC 0.20 Trp LoE Film (55) Bronze 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | BRONZE 6MM | AIR 13MM | COATED POLY-55 | AIR 13MM | CLEAR 3MM
U 0.20 SHGC 0.19 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.20 SHGC 0.19 Simple Glazing
U 0.20 SHGC 0.20 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.20 SHGC 0.20 Simple Glazing
U 0.20 SHGC 0.21 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.20 SHGC 0.21 Simple Glazing
U 0.20 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.20 SHGC 0.22 Simple Glazing
U 0.23 SHGC 0.31 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.23 SHGC 0.31 Simple Glazing
U 0.23 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.23 SHGC 0.34 Simple Glazing
U 0.24 SHGC 0.11 Dbl LoE Elec Abs Colored 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | ECABS-2 COLORED 6MM | ARGON 13MM | LoE SPEC SEL CLEAR 6MM Rev
U 0.24 SHGC 0.16 Dbl Elec Abs Colored 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | ECABS-2 COLORED 6MM | ARGON 13MM | CLEAR 6MM
U 0.24 SHGC 0.23 Dbl LoE Spec Sel Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | LoE SPEC SEL TINT 6MM | ARGON 13MM | CLEAR 6MM
U 0.25 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.25 SHGC 0.22 Simple Glazing
U 0.25 SHGC 0.24 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.25 SHGC 0.24 Simple Glazing
U 0.25 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | ARGON 13MM | CLEAR 6MM
U 0.26 SHGC 0.40 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.26 SHGC 0.40 Simple Glazing
U 0.29 SHGC 0.11 Dbl LoE Elec Ref Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | ECREF-2 COLORED 6MM | AIR 13MM | LoE SPEC SEL CLEAR 6MM Rev
U 0.29 SHGC 0.17 Dbl Elec Abs Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | ECABS-2 COLORED 6MM | AIR 13MM | CLEAR 6MM
U 0.29 SHGC 0.22 Trp LoE Film (55) Bronze 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | BRONZE 6MM | AIR 6MM | COATED POLY-55 | AIR 6MM | CLEAR 3MM
U 0.29 SHGC 0.40 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.29 SHGC 0.40 Simple Glazing
U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM
U 0.32 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.32 SHGC 0.36 Simple Glazing
U 0.33 SHGC 0.11 Dbl LoE Elec Ref Colored 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | ECREF-2 COLORED 6MM | AIR 13MM | LoE SPEC SEL CLEAR 6MM Rev
U 0.33 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM
U 0.33 SHGC 0.45 Trp LoE Film (77) Clr 3mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | CLEAR 3MM | AIR 6MM | COATED POLY-77 | AIR 6MM | CLEAR 3MM
U 0.34 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.34 SHGC 0.38 Simple Glazing
U 0.34 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM
U 0.34 SHGC 0.45 Dbl LoE (e2-.2) Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | PYR B CLEAR 6MM | AIR 13MM | CLEAR 6MM
U 0.35 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.35 SHGC 0.22 Simple Glazing
U 0.35 SHGC 0.24 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.35 SHGC 0.24 Simple Glazing
U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR MID 6MM | ARGON 13MM | CLEAR 6MM
U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 13MM | CLEAR 6MM
U 0.36 SHGC 0.35 Dbl LoE Spec Sel Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE SPEC SEL TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.36 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.36 SHGC 0.36 Simple Glazing
U 0.36 SHGC 0.38 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.36 SHGC 0.38 Simple Glazing
U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | REF B TINT HI 6MM | ARGON 13MM | CLEAR 6MM
U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM | ARGON 13MM | CLEAR 6MM
U 0.39 SHGC 0.32 | ExteriorWindow | Metal framing (all other) |  |  | Theoretical Glass 347
U 0.39 SHGC 0.38 | ExteriorWindow | Metal framing (all other) |  |  | Theoretical Glass 297
U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE SPEC SEL CLEAR 3MM | AIR 6MM | CLEAR 6MM
U 0.40 SHGC 0.45 | ExteriorWindow | Metal framing (all other) |  |  | ECABS-2 BLEACHED 6MM | AIR 6MM | LoE SPEC SEL CLEAR 6MM Rev
U 0.42 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.42 SHGC 0.25 Simple Glazing
U 0.42 SHGC 0.34 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.42 SHGC 0.34 Simple Glazing
U 0.42 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM | ARGON 13MM | CLEAR 6MM
U 0.43 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM
U 0.43 SHGC 0.29 Dbl LoE Spec Sel Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | LoE SPEC SEL TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF B TINT HI 6MM | AIR 13MM | CLEAR 6MM
U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM
U 0.45 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.45 SHGC 0.25 Simple Glazing
U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM | AIR 13MM | CLEAR 6MM
U 0.45 SHGC 0.33 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.45 SHGC 0.33 Simple Glazing
U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | GREY 6MM | AIR 13MM | CLEAR 6MM
U 0.47 SHGC 0.33 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.47 SHGC 0.33 Simple Glazing
U 0.48 SHGC 0.19 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.48 SHGC 0.19 Simple Glazing
U 0.48 SHGC 0.21 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.48 SHGC 0.21 Simple Glazing
U 0.48 SHGC 0.20 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.48 SHGC 0.20 Simple Glazing
U 0.48 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.48 SHGC 0.22 Simple Glazing
U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM
U 0.50 SHGC 0.22 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.50 SHGC 0.22 Simple Glazing
U 0.50 SHGC 0.23 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.50 SHGC 0.23 Simple Glazing
U 0.52 SHGC 0.22 Dbl Ref-B-L Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR LO 6MM | AIR 6MM | CLEAR 6MM
U 0.52 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.52 SHGC 0.39 Simple Glazing
U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM | AIR 13MM | CLEAR 6MM
U 0.52 SHGC 0.49 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.52 SHGC 0.49 Simple Glazing
U 0.52 SHGC 0.615 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.52 SHGC 0.615 Simple Glazing
U 0.54 SHGC 0.13 Dbl Ref-A-L Clr 6mm/13mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF A CLEAR LO 6MM | AIR 13MM | CLEAR 6MM
U 0.54 SHGC 0.18 Dbl Ref-A-M Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF A TINT MID 6MM | AIR 6MM | CLEAR 6MM
U 0.54 SHGC 0.23 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.54 SHGC 0.23 Simple Glazing
U 0.54 SHGC 0.27 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
U 0.55 SHGC 0.25 | ExteriorWindow | Metal framing (all other) |  |  | Glass_2175_LayerAvg | Gap_1_W_0_0032 | Glass_2022F_LayerAvg
U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF D TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.56 SHGC 0.35 Dbl Ref-D Tint 6mm/6mm | ExteriorWindow | Metal framing (all other) |  |  | REF D TINT 6MM | AIR 6MM | CLEAR 6MM
U 0.56 SHGC 0.76 Dbl Clr 3mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | CLEAR 3MM | AIR 6MM | CLEAR 3MM
U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM
U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | BLUE 6MM | AIR 6MM | CLEAR 6MM
U 0.59 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.59 SHGC 0.36 Simple Glazing
U 0.59 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.59 SHGC 0.39 Simple Glazing
U 0.60 SHGC 0.23 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.60 SHGC 0.23 Simple Glazing
U 0.62 SHGC 0.20 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.62 SHGC 0.20 Simple Glazing
U 0.62 SHGC 0.21 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.62 SHGC 0.21 Simple Glazing
U 0.62 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
U 0.62 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM | AIR 6MM | CLEAR 6MM
U 0.62 SHGC 0.41 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.62 SHGC 0.41 Simple Glazing
U 0.62 SHGC 0.49 Dbl Blue 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | BLUE 6MM | AIR 6MM | CLEAR 6MM
U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm | ExteriorWindow | Metal framing (all other) |  |  | PYR B CLEAR 3MM
U 0.71 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM | AIR 6MM | CLEAR 6MM
U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B TINT MID 6MM
U 0.72 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.72 SHGC 0.25 Simple Glazing
U 0.72 SHGC 0.36 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.72 SHGC 0.36 Simple Glazing
U 0.72 SHGC 0.39 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 0.72 SHGC 0.39 Simple Glazing
U 0.75 SHGC 0.72 Sgl LoE (e2-.2) Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | PYR B CLEAR 6MM
U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF A CLEAR LO 6MM
U 0.88 SHGC 0.27 Sgl Elec Ref Colored 6mm | ExteriorWindow | Metal framing (all other) |  |  | ECREF-1 COLORED 6MM
U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM
U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM
U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM
U 1.17 SHGC 0.49 Sgl Ref-D Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF D CLEAR 6MM
U 1.17 SHGC 0.68 Sgl Green 3mm | ExteriorWindow | Metal framing (all other) |  |  | GREEN 3MM
U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm | ExteriorWindow | Metal framing (all other) |  |  | ECREF-1 COLORED 6MM
U 1.22 SHGC 0.25 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 1.22 SHGC 0.25 Simple Glazing
U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF C CLEAR HI 6MM
U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM
U 1.22 SHGC 0.54 Simple Glazing Window | ExteriorWindow | Metal framing (all other) |  |  | U 1.22 SHGC 0.54 Simple Glazing
U 1.22 SHGC 0.61 Sgl Green 6mm | ExteriorWindow | Metal framing (all other) |  |  | GREEN 6MM
U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm | ExteriorWindow | Metal framing (all other) |  |  | REF B CLEAR HI 6MM
U 1.98 SHGC 0.61 Sgl Green 6mm | ExteriorWindow | Metal framing (all other) |  |  | GREEN 6MM
U0.47_SHGC_0.49_SimpleGlazing_Window_05 | ExteriorWindow |  |  |  | U0.47_SHGC_0.49_SimpleGlazing_Window_05
U0.47_SHGC0.46_SimpleGlazing_Window_07 | ExteriorWindow |  |  |  | U0.47_SHGC0.46_SimpleGlazing_Window_07
U0.47_SHGC0.47_SimpleGlazing_Window_06 | ExteriorWindow |  |  |  | U0.47_SHGC0.47_SimpleGlazing_Window_06
U0.47_SHGC0.47_SimpleGlazing_Window_11 | ExteriorWindow |  |  |  | U0.47_SHGC0.47_SimpleGlazing_Window_11
U0.47_SHGC0.5_SimpleGlazing_Window_03 | ExteriorWindow |  |  |  | U0.47_SHGC0.5_SimpleGlazing_Window_03
U0.77_SHGC_0.77_SimpleGlazing_Window_02 | ExteriorWindow |  |  |  | U0.77_SHGC_0.77_SimpleGlazing_Window_02
U0.77_SHGC0.5_SimpleGlazing_Window_09 | ExteriorWindow |  |  |  | U0.77_SHGC0.5_SimpleGlazing_Window_09
U0.77_SHGC0.61_SimpleGlazing_Window_08 | ExteriorWindow |  |  |  | U0.77_SHGC0.61_SimpleGlazing_Window_08
U0.77_SHGC0.62_SimpleGlazing_Window_04 | ExteriorWindow |  |  |  | U0.77_SHGC0.62_SimpleGlazing_Window_04
U1.23_SHGC0.5_SimpleGlazing_Window_12 | ExteriorWindow |  |  |  | U1.23_SHGC0.5_SimpleGlazing_Window_12
U1.23_SHGC0.82_SimpleGlazing_Window_01 | ExteriorWindow |  |  |  | U1.23_SHGC0.82_SimpleGlazing_Window_01
U1.23_SHGC0.82_SimpleGlazing_Window_10 | ExteriorWindow |  |  |  | U1.23_SHGC0.82_SimpleGlazing_Window_10
Adiabatic GroundContactFloor | GroundContactFloor | Mass |  |  | Adiabatic Material
ext-slab | GroundContactFloor | Mass |  |  | 6 in. Normalweight Concrete Floor
ext-slab-mass | GroundContactFloor | Mass | CP02 CARPET PAD |  | HW CONCRETE | CP02 CARPET PAD
ext-slab-metal-building | GroundContactFloor | Metal Building |  |  | HW CONCRETE 8 in
ext-slab-steel-frame | GroundContactFloor | SteelFramed | CP02 CARPET PAD |  | HW CONCRETE 8 in | CP02 CARPET PAD
Ground FloorGround_Floor_R11_T2013 | GroundContactFloor |  |  |  | Ground_Floor_R11_T2013 | Plywood - 5/8 in. CBES | Carpet - 3/4 in. CBES
Ground FloorGround_Floor_R17_T2013 | GroundContactFloor |  |  |  | Ground_Floor_R17_T2013 | Plywood - 5/8 in. CBES | Carpet - 3/4 in. CBES
Ground FloorGround_Floor_R22_T2013 | GroundContactFloor |  |  |  | Ground_Floor_R22_T2013 | Plywood - 5/8 in. CBES | Carpet - 3/4 in. CBES
Smallhotel 2010 Slab Floor | GroundContactFloor | Mass | Typical Insulation |  | 8 in. Normalweight Concrete Floor | CP02 CARPET PAD
Typical Carpeted 6in Slab Floor | GroundContactFloor | Mass |  |  | 6 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Carpeted 8in Slab Floor | GroundContactFloor | Mass |  |  | 8 in. Concrete Block Basement Wall | Typical Carpet Pad
Typical Insulated 6in Slab Floor | GroundContactFloor | Mass | Typical Insulation |  | Typical Insulation | 6 in. Normalweight Concrete Floor
Typical Insulated 8in Slab Floor | GroundContactFloor | Mass | Typical Insulation |  | Typical Insulation | 8 in. Normalweight Concrete Floor
Typical Insulated Carpeted 6in Slab Floor | GroundContactFloor | Mass | Typical Insulation |  | Typical Insulation | 6 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Insulated Carpeted 8in Slab Floor | GroundContactFloor | Mass | Typical Insulation |  | Typical Insulation | 8 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Uncarpeted 6in Slab Floor | GroundContactFloor | Mass |  |  | 6 in. Normalweight Concrete Floor
Typical Uninsulated 6in Slab Floor | GroundContactFloor | Mass |  |  | 6 in. Normalweight Concrete Floor
Typical Uninsulated 8in Slab Floor | GroundContactFloor | Mass |  |  | 8 in. Normalweight Concrete Floor
Typical Uninsulated Carpeted 8in Slab Floor | GroundContactFloor | Mass |  |  | 8 in. Concrete Block Basement Wall | Typical Carpet Pad
Typical Unisulated Carpeted 6in Slab Floor | GroundContactFloor | Mass |  |  | 6 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Insulated Basement Mass Wall | GroundContactWall | Mass | Typical Insulation |  | Typical Insulation | 8 in. Concrete Block Basement Wall
Typical Uninsulated Basement Mass Wall | GroundContactWall | Mass |  |  | 8 in. Concrete Block Basement Wall
ceiling_Metal roof | InteriorCeiling |  |  |  | Metal Standing Seam - 1/16 in. | ceiling_2_Insulation
int_slab_ceiling_smallhotel | InteriorCeiling |  |  |  | CP02 CARPET PAD | 4 in. Normalweight Concrete Floor
LargeHotel Interior Ceiling | InteriorCeiling |  |  |  | CP02 CARPET PAD | 100mm Normalweight concrete floor | Nonres_Floor_Insulation | G01 13mm gypsum board
NACM_Drop Ceiling | InteriorCeiling |  |  |  | Acoustic Ceiling
Plenum Acoustical Tile | InteriorCeiling |  |  |  | Acoustic Tile - 1/2 in.
Typical Interior Ceiling | InteriorCeiling |  |  |  | CP02 CARPET PAD | 100mm Normalweight concrete floor
Typical Interior Door | InteriorDoor |  |  |  | G05 25mm wood
int_slab_floor_smallhotel | InteriorFloor |  |  |  | 4 in. Normalweight Concrete Floor | CP02 CARPET PAD
LargeHotel Interior Floor | InteriorFloor |  |  |  | G01 13mm gypsum board | Nonres_Floor_Insulation | 100mm Normalweight concrete floor | CP02 CARPET PAD
NACM_Interior Floor | InteriorFloor |  |  |  | NACM_Carpet 3/4in
Typical Interior Floor | InteriorFloor |  |  |  | 100mm Normalweight concrete floor | CP02 CARPET PAD
Typical Interior Slab Floor | InteriorFloor | Mass |  |  | 4 in. Normalweight Concrete Floor | Typical Carpet Pad
Typical Interior Partition | InteriorPartition |  |  |  | G05 25mm wood
Uninsulated Steel Stud Wall | InteriorPartition | SteelFramed |  |  | Metal Framed Wall - 24inOC - 2x4 - R0 ins.
int_wall_smallhotel | InteriorWall |  |  |  | 1/2 in. Gypsum Board | 1/2 in. Gypsum Board
LargeHotel Interior Wall | InteriorWall |  |  |  | G01 13mm gypsum board | G01 13mm gypsum board
NACM_Interior Wall | InteriorWall |  |  |  | NACM_Gypsum Board 5/8in | NACM_Gypsum Board 5/8in
Typical Insulated Interior Wall | InteriorWall | WoodFramed | Typical Insulation |  | 25mm Stucco | 5/8 in. Gypsum Board | Typical Insulation | Steel Frame/Cavity | 5/8 in. Gypsum Board
Typical Interior Wall | InteriorWall |  |  |  | G01 13mm gypsum board | G01 13mm gypsum board
Typical Uninsulated Interior Wall | InteriorWall | WoodFramed |  |  | 1/2 in. Gypsum Board | 1/2 in. Gypsum Board
Typical Interior Window | InteriorWindow |  |  |  | Clear 3mm
U 0.58 SHGC 0.19 Simple Glazing Skylight | Skylight | Glass with Curb |  |  | U 0.58 SHGC 0.19 Simple Glazing
U 0.58 SHGC 0.36 Simple Glazing Skylight | Skylight | Glass with Curb |  |  | U 0.58 SHGC 0.36 Simple Glazing
U 1.98 SHGC 0.61 Simple Glazing Skylight | Skylight | Glass with Curb |  |  | U 1.98 SHGC 0.61 Simple Glazing
Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.000_in | Skylight |  |  | Skylight_Frame_Width_0.000_in | Glass_2052_LayerAvg | Gap_1_W_0_0038 | Glass_2027F_LayerAvg
Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.334_in | Skylight |  |  | Skylight_Frame_Width_0.334_in | Glass_2052_LayerAvg | Gap_1_W_0_0038 | Glass_2027F_LayerAvg
Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.430_in | Skylight |  |  | Skylight_Frame_Width_0.430_in | Glass_2052_LayerAvg | Gap_1_W_0_0038 | Glass_2027F_LayerAvg
Window_U_0.55_SHGC_0.35_Skylight_Frame_Width_0.709_in | Skylight |  |  | Skylight_Frame_Width_0.709_in | Glass_2052_LayerAvg | Gap_1_W_0_0038 | Glass_2027F_LayerAvg
Window_U_0.65_SHGC_0.35_Skylight_Frame_Width_2.339_in | Skylight |  |  | Skylight_Frame_Width_2.339_in | Glass_2052_LayerAvg | Gap_1_W_0_0024 | Glass_2027F_LayerAvg
Window_U_0.75_SHGC_0.35_Skylight_Frame_Width_2.339_in | Skylight |  |  | Skylight_Frame_Width_2.339_in | Glass_2052_LayerAvg | Gap_1_W_0_0018 | Glass_2027F_LayerAvg
U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  |  | Glass_2175_LayerAvg | Gap_1_W_0_0025 | Glass_2022F_LayerAvg
U 0.61 SHGC 0.77 Simple Glazing Skylight |  |  |  |  | U 0.61 SHGC 0.77 Simple Glazing
U 0.65 SHGC 0.35 Simple Glazing Skylight |  |  |  |  | U 0.65 SHGC 0.35 Simple Glazing
U 0.69 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.19 Simple Glazing
U 0.69 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.36 Simple Glazing
U 0.69 SHGC 0.39 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.39 Simple Glazing
U 0.69 SHGC 0.49 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.49 Simple Glazing
U 0.69 SHGC 0.64 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.64 Simple Glazing
U 0.69 SHGC 0.68 Simple Glazing Skylight |  |  |  |  | U 0.69 SHGC 0.68 Simple Glazing
U 0.74 SHGC 0.55 Simple Glazing Skylight |  |  |  |  | U 0.74 SHGC 0.55 Simple Glazing
U 0.74 SHGC 0.65 Simple Glazing Skylight |  |  |  |  | U 0.74 SHGC 0.65 Simple Glazing
U 0.75 SHGC 0.35 Simple Glazing Skylight |  |  |  |  | U 0.75 SHGC 0.35 Simple Glazing
U 0.81 SHGC 0.65 Simple Glazing Skylight |  |  |  |  | U 0.81 SHGC 0.65 Simple Glazing
U 0.85 SHGC 0.65 Simple Glazing Skylight |  |  |  |  | U 0.85 SHGC 0.65 Simple Glazing
U 0.87 SHGC 0.58 Simple Glazing Skylight |  |  |  |  | U 0.87 SHGC 0.58 Simple Glazing
U 0.87 SHGC 0.71 Simple Glazing Skylight |  |  |  |  | U 0.87 SHGC 0.71 Simple Glazing
U 0.87 SHGC 0.77 Simple Glazing Skylight |  |  |  |  | U 0.87 SHGC 0.77 Simple Glazing
U 0.98 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | U 0.98 SHGC 0.19 Simple Glazing
U 0.98 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 0.98 SHGC 0.36 Simple Glazing
U 1.10 SHGC 0.62 Simple Glazing Skylight |  |  |  |  | U 1.10 SHGC 0.62 Simple Glazing
U 1.10 SHGC 0.77 Simple Glazing Skylight |  |  |  |  | U 1.10 SHGC 0.77 Simple Glazing
U 1.15 SHGC 0.77 Simple Glazing Skylight |  |  |  |  | U 1.15 SHGC 0.77 Simple Glazing
U 1.17 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.19 Simple Glazing
U 1.17 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.36 Simple Glazing
U 1.17 SHGC 0.39 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.39 Simple Glazing
U 1.17 SHGC 0.49 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.49 Simple Glazing
U 1.17 SHGC 0.64 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.64 Simple Glazing
U 1.17 SHGC 0.68 Simple Glazing Skylight |  |  |  |  | U 1.17 SHGC 0.68 Simple Glazing
U 1.30 SHGC 0.27 Simple Glazing Skylight |  |  |  |  | U 1.30 SHGC 0.27 Simple Glazing
U 1.30 SHGC 0.34 Simple Glazing Skylight |  |  |  |  | U 1.30 SHGC 0.34 Simple Glazing
U 1.30 SHGC 0.62 Simple Glazing Skylight |  |  |  |  | U 1.30 SHGC 0.62 Simple Glazing
U 1.30 SHGC 0.65 Simple Glazing Skylight |  |  |  |  | U 1.30 SHGC 0.65 Simple Glazing
U 1.36 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | U 1.36 SHGC 0.19 Simple Glazing
U 1.36 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 1.36 SHGC 0.36 Simple Glazing
U 1.36 SHGC 0.39 Simple Glazing Skylight |  |  |  |  | U 1.36 SHGC 0.39 Simple Glazing
U 1.36 SHGC 0.61 Simple Glazing Skylight |  |  |  |  | U 1.36 SHGC 0.61 Simple Glazing
U 1.70 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 1.70 SHGC 0.36 Simple Glazing
U 1.80 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 1.80 SHGC 0.36 Simple Glazing
U 1.90 SHGC 0.27 Simple Glazing Skylight |  |  |  |  | U 1.90 SHGC 0.27 Simple Glazing
U 1.90 SHGC 0.34 Simple Glazing Skylight |  |  |  |  | U 1.90 SHGC 0.34 Simple Glazing
U 1.90 SHGC 0.39 Simple Glazing Skylight |  |  |  |  | U 1.90 SHGC 0.39 Simple Glazing
U 1.90 SHGC 0.65 Simple Glazing Skylight |  |  |  |  | U 1.90 SHGC 0.65 Simple Glazing
U 1.98 SHGC 0.16 Simple Glazing Skylight |  |  |  |  | U 1.98 SHGC 0.16 Simple Glazing
U 1.98 SHGC 0.19 Simple Glazing Skylight |  |  |  |  | U 1.98 SHGC 0.19 Simple Glazing
U 1.98 SHGC 0.36 Simple Glazing Skylight |  |  |  |  | U 1.98 SHGC 0.36 Simple Glazing
U 1.98 SHGC 0.39 Simple Glazing Skylight |  |  |  |  | U 1.98 SHGC 0.39 Simple Glazing

## Construction Sets
A Construction Set lists the typical constructions for each surface type in a building for a given building type and climate zone.
|  |  |  | Exterior Surfaces | [5 empty] | Interior Surfaces |  |  | Ground Contact Surfaces | [5 empty] | Exterior Sub Surfaces | [13 empty] | Interior Sub Surfaces |  |  | Misc Surfaces
Template | Building Type | Space Type | Is Residential | Exterior Wall Standards Construction Type | Exterior Wall Building Category | Exterior Floor Standards Construction Type | Exterior Floor Building Category | Exterior Roof Standards Construction Type | Exterior Roof Building Category | Interior Walls | Interior Floors | Interior Ceilings | Ground Contact Wall Standards Construction Type | Ground Contact Wall Building Category | Ground Contact Floor Standards Construction Type | Ground Contact Floor Building Category | Ground Contact Ceiling Standards Construction Type | Ground Contact Ceiling Building Category | Exterior Fixed Window Standards Construction Type | Exterior Fixed Window Building Category | Exterior Operable Window Standards Construction Type | Exterior Operable Window Building Category | Exterior Door Standards Construction Type | Exterior Door Building Category | Exterior Glass Door Standards Construction Type | Exterior Glass Door Building Category | Exterior Overhead Door Standards Construction Type | Exterior Overhead Door Building Category | Exterior Skylight Standards Construction Type | Exterior Skylight Building Category | Tubular Daylight Domes | Tubular Daylight Diffusers | Interior Fixed Windows | Interior Operable Windows | Interior Doors | Space Shading | Building Shading | Site Shading | Interior Partitions | Notes
189.1-2009 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SmallOffice |  | No | Mass | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
189.1-2009 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
189.1-2009 | SmallOfficeDetailed |  | No | Mass | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
189.1-2009 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | HighriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
90.1-2004 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
90.1-2004 | SmallDataCenterLowITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2004 | SmallDataCenterHighITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2004 | LargeDataCenterLowITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2004 | LargeDataCenterHighITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2004 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | SmallOfficeDetailed |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2004 | Laboratory |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | HighriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
90.1-2007 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
90.1-2007 | SmallDataCenterLowITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2007 | SmallDataCenterHighITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2007 | LargeDataCenterLowITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2007 | LargeDataCenterHighITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2007 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | SmallOfficeDetailed |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2007 | Laboratory |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | HighriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
90.1-2010 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
90.1-2010 | SmallDataCenterLowITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2010 | SmallDataCenterHighITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2010 | LargeDataCenterLowITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2010 | LargeDataCenterHighITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2010 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | SmallOfficeDetailed |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2010 | Laboratory |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | HighriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Hospital | PatRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeHotel | GuestRoom | No | Mass | Residential | Mass | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallHotel |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | int_wall_smallhotel | int_slab_floor_smallhotel | int_slab_ceiling_smallhotel | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
90.1-2013 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
90.1-2013 | SmallDataCenterLowITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2013 | SmallDataCenterHighITE |  | No | Mass | Adiabatic | Mass | Adiabatic | Attic and Other | Adiabatic | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Mass | Adiabatic
90.1-2013 | LargeDataCenterLowITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2013 | LargeDataCenterHighITE |  | No | SteelFramed | Nonresidential | SteelFramed | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  |  | Unheated | Nonresidential
90.1-2013 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | SmallOfficeDetailed |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
90.1-2013 | Laboratory |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | College |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Uninsulated Steel Stud Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential | Glass with Curb | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition | listed as "Crawl" (crawlspace) in DEER
DOE Ref 1980-2004 | Hospital | PatRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeHotel | GuestRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | SteelFramed | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition | Note "occupied' as default spacetype
DOE Ref 1980-2004 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Retail |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SmallOffice |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | Metal Building | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | Metal Building | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
DOE Ref 1980-2004 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
DOE Ref 1980-2004 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | SmallOfficeDetailed |  | No | WoodFramed | Nonresidential | Mass | Residential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref 1980-2004 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Courthouse |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Hospital |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Hospital | PatRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeHotel |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition | listed as "Crawl" (crawlspace) in DEER
DOE Ref Pre-1980 | LargeHotel | GuestRoom | No | Mass | Nonresidential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeOffice |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | MediumOffice |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | MidriseApartment |  | No | SteelFramed | Residential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Office |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Outpatient |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | SteelFramed | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | PrimarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | QuickServiceRestaurant |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Retail |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition | Note "occupied' as default spacetype
DOE Ref Pre-1980 | SecondarySchool |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SmallHotel |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SmallOffice |  | No | SteelFramed | Nonresidential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | StripMall |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SuperMarket |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Warehouse |  | No | Metal Building | Semiheated | Mass | Nonresidential | IEAD | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Warehouse | Office | No | Metal Building | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Warehouse | Fine | No | Metal Building | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Unheated | Semiheated |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Warehouse | Bulk | No | Metal Building | Semiheated | Mass | Nonresidential | IEAD | Semiheated | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Semiheated | Unheated | Semiheated |  | Semiheated | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Semiheated |  |  | NonSwinging | Semiheated |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | Any | Attic | No |  | Nonresidential | WoodFramed | Nonresidential | Attic and Other | Nonresidential |  | Plenum Acoustical Tile
DOE Ref Pre-1980 | Any | Plenum | No |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
DOE Ref Pre-1980 | MediumOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | SmallOfficeDetailed |  | No | SteelFramed | Nonresidential | Mass | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
DOE Ref Pre-1980 | LargeOfficeDetailed |  | No | Mass | Nonresidential | Mass | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Nonresidential | Mass | Nonresidential |  | Nonresidential | Metal framing (all other) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential | Metal framing (entrance door) | Nonresidential | NonSwinging | Nonresidential |  |  | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ICC IECC 2015 | MidriseApartment |  | Yes | SteelFramed | Residential | Mass | Residential | IEAD | Residential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling | Mass | Residential | Unheated | Residential |  | Residential | Metal framing (all other) | Residential | Metal framing (all other) | Residential | Swinging | Residential |  |  | NonSwinging | Residential | Glass with Curb | Residential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | FullServiceRestaurant |  | No | SteelFramed | Nonresidential |  | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | LargeHotel |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | LargeHotel | GuestRoom | No | SteelFramed | Residential |  | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | MidriseApartment |  | No | WoodFramed | Residential |  | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | Office |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential |  | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | Retail |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | StripMall |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
NREL ZNE Ready 2017 | Any | Plenum |  |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile
ZE AEDG Multifamily | FullServiceRestaurant |  | No | SteelFramed | Nonresidential |  | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | LargeHotel |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | LargeHotel | GuestRoom | No | SteelFramed | Residential |  | Residential | IEAD | Residential | LargeHotel Interior Wall | LargeHotel Interior Floor | LargeHotel Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | MidriseApartment |  | No | WoodFramed | Residential |  | Residential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | Office |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | QuickServiceRestaurant |  | No | WoodFramed | Nonresidential |  | Nonresidential | Attic and Other | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | Retail |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | StripMall |  | No | SteelFramed | Nonresidential |  | Nonresidential | IEAD | Nonresidential | Typical Interior Wall | Typical Interior Floor | Typical Interior Ceiling |  | Nonresidential | Unheated | Nonresidential |  | Nonresidential | Metal framing (curtainwall/storefront) | Nonresidential | Metal framing (all other) | Nonresidential | Swinging | Nonresidential |  | Nonresidential | NonSwinging | Nonresidential |  | Nonresidential | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Window | Typical Interior Door |  |  |  | Typical Interior Partition
ZE AEDG Multifamily | Any | Plenum |  |  | Nonresidential |  | Nonresidential |  | Nonresidential |  | Plenum Acoustical Tile

## Construction Properties
This table contains construction requirements for different classes of constructions
Template | Climate Zone Set | Operation Type | Intended Surface Type | Standards Construction Type | Building Category | Construction | Orientation | Minimum Percent of Surface | Maximum Percent of Surface | Assembly Maximum U-Value | U-Value Includes Interior Film Coefficient | U-Value Includes Exterior Film Coefficient | Assembly Maximum F Factor | Assembly Maximum C Factor | Assembly Maximum Solar Heat Gain Coefficient | Assembly Minimum VT SHGC | Notes
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.50 SHGC 0.22 Simple Glazing Window |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.22 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.20 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.2 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.50 SHGC 0.22 Simple Glazing Window |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.22 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.62 SHGC 0.20 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.2 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 0 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.50 SHGC 0.23 Simple Glazing Window |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.21 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.21 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.50 SHGC 0.23 Simple Glazing Window |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.62 SHGC 0.21 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.21 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 1.282 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.614 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 1.28 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 1.18 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.167 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.17
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 2 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 2 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 2 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 2 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 2 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 2 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 2 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 2 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 2 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 3 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 3A |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 3A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 3B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 0.72 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 0.72 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 0.72 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.34 Sgl Ref-C-H Clr 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Simple Glazing Window |  | 40.001 | 100 | 0.72 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.61 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 3C |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.61 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 3C |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2004 | ClimateZone 3C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.134 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 4 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 4 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 4 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 4 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 4 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 4 |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2004 | ClimateZone 4 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
90.1-2004 | ClimateZone 4 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 4 |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 4 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.0066 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.26
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 6 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2004 | ClimateZone 6 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 6 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
90.1-2004 | ClimateZone 6 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.65
90.1-2004 | ClimateZone 6 |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 6 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 6 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.61
90.1-2004 | ClimateZone 6 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 1 | 10 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 10.001 | 20 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 20.001 | 30 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 30.001 | 40 | 0.57 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  | 40.001 | 100 | 0.46 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2004 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.055 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 1 | 10 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 10.001 | 20 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 20.001 | 30 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  | 30.001 | 40 | 0.46 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  | 40.001 | 100 | 0.35 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.62
90.1-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.49
90.1-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
90.1-2004 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.81 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE |  |  | 0.25
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  | 40.001 | 100 | 1.22 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 1 | 10 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 10.001 | 20 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 20.001 | 30 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  | 30.001 | 40 | 1.22 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.98 SHGC 0.68 Sgl Ref-B-H Clr 6mm |  | 40.001 | 100 | 0.98 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
90.1-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
90.1-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.16
90.1-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.34
90.1-2004 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.27
90.1-2004 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.063 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 1.28 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.167 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.7 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.7 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 2 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 2 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 2 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 2 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 2 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.39
90.1-2007 | ClimateZone 2 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 2 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 2 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.46
90.1-2007 | ClimateZone 2 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.09
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 3 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 3 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 3 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.71
90.1-2007 | ClimateZone 3 |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.65
90.1-2007 | ClimateZone 3 |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.55
90.1-2007 | ClimateZone 3 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2007 | ClimateZone 3 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 3 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.5 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.134 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.39 SHGC 0.38 |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.39 SHGC 0.38 |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.85 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.85 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 4 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 4 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 4 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
90.1-2007 | ClimateZone 4 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.68
90.1-2007 | ClimateZone 4 |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.64
90.1-2007 | ClimateZone 4 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.64
90.1-2007 | ClimateZone 4 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 4 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.77
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.119 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.77
90.1-2007 | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.77
90.1-2007 | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.68
90.1-2007 | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.64
90.1-2007 | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.64
90.1-2007 | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2007 | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2007 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 6 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 6 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 6 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 6 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.042 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.843
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092
90.1-2007 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.36
90.1-2007 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.19
90.1-2007 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.16
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.036 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.052 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.037 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.036 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.45
90.1-2007 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2007 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.075
90.1-2007 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.34
90.1-2007 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.27
90.1-2007 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.27
90.1-2007 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.36
90.1-2007 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.81 | TRUE | TRUE |  |  | 0.19
90.1-2007 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 1.18 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2007 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2007 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.49
90.1-2007 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.39
90.1-2007 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2007 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.77
90.1-2007 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.77
90.1-2007 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.62
90.1-2007 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.065 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.063 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.065 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.167 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.7 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.7 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.75 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 2 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 2 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 2 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
90.1-2010 | ClimateZone 2 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
90.1-2010 | ClimateZone 2 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 2 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 2 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 2 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 2 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Unheated | Nonresidential | Smallhotel 2010 Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Heated | Nonresidential | Smallhotel 2010 Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Unheated | Residential | Smallhotel 2010 Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Heated | Residential | Smallhotel 2010 Slab Floor |  |  |  |  | TRUE | TRUE | 0.09
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 3 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 3 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 3 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
90.1-2010 | ClimateZone 3 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 3 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 3 |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2010 | ClimateZone 3 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
90.1-2010 | ClimateZone 3 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
90.1-2010 | ClimateZone 3 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
90.1-2010 | ClimateZone 3 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.097 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.39 SHGC 0.38 |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.39 SHGC 0.38 |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.85 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.85 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 4 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 4 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 4 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.39
90.1-2010 | ClimateZone 4 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 4 |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 4 |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2010 | ClimateZone 4 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 4 |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 4 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.055 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.119 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.083 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Sgl Ref-D Clr 6mm |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
90.1-2010 | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.62
90.1-2010 | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.27
90.1-2010 | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2010 | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.069 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  |  |  | 0.55 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.4
90.1-2010 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 6 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 6 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 6 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 6 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 6 |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 6 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.39
90.1-2010 | ClimateZone 6 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 6 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.77
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.042 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.843
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092
90.1-2010 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | U 1.17 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.77
90.1-2010 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.62
90.1-2010 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
90.1-2010 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
90.1-2010 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Uninsulated Swinging Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.035 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.035 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.036 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.052 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.037 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.036 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.42 SHGC 0.45 Dbl Ref-D Clr 6mm/13mm Arg |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE |  |  | 0.45
90.1-2010 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.8 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.9 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2010 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.075
90.1-2010 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.49
90.1-2010 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.46
90.1-2010 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
90.1-2010 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.71
90.1-2010 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.65
90.1-2010 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.55
90.1-2010 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.81 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.093 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE | 0.73
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2010 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.36
90.1-2010 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
90.1-2010 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
90.1-2010 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.048 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof - Highly Reflective |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.218 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1156 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.173 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.096 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.162 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | 0.83 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.93 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.83 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 2 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 2 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 2 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 2 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.65_SHGC_0.35_Skylight_Frame_Width_2.339_in |  | 0 | 2 | 0.65 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | Skylight | Glass with Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.65 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | Skylight | Glass with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE |  |  | 0.77
90.1-2013 | ClimateZone 2 |  | Skylight | Plastic with Curb | Nonresidential | U 0.65 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.65 | TRUE | TRUE |  |  | 0.77
90.1-2013 | ClimateZone 2 |  | Skylight | Plastic with Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.65 | TRUE | TRUE |  |  | 0.77
90.1-2013 | ClimateZone 2 |  | Skylight | Plastic with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | Skylight | Without Curb | Nonresidential | U 0.65 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.65 | TRUE | TRUE
90.1-2013 | ClimateZone 2 |  | Skylight | Without Curb | Residential | U 0.65 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.65 | TRUE | TRUE |  |  | 0.68
90.1-2013 | ClimateZone 2 |  | Skylight | Without Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE |  |  | 0.64
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof - Highly Reflective |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.041 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.119 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.096 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.077 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.072 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.162 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.55 SHGC 0.25 |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.26 Dbl Ref-C-M Clr 6mm/13mm Arg |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.87 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 3 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.17 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.2 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 3 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 3 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 3 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.55_SHGC_0.35_Skylight_Frame_Width_0.709_in |  | 0 | 2 | 0.55 | TRUE | TRUE |  |  | 0.64
90.1-2013 | ClimateZone 3 |  | Skylight | Glass with Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  | 0 | 2 | 0.55 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Glass with Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.7 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Plastic with Curb | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  | 0 | 2 | 0.55 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Plastic with Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  | 0 | 2 | 0.55 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Plastic with Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.7 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Without Curb | Nonresidential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  | 0 | 2 | 0.55 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Without Curb | Residential | U 0.55 SHGC 0.31 Dbl Ref-D Tint 6mm/6mm Air |  | 0 | 2 | 0.55 | TRUE | TRUE
90.1-2013 | ClimateZone 3 |  | Skylight | Without Curb | Semiheated | U 1.70 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.7 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.093 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.082 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.06 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.162 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.35 SHGC 0.35 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.51 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.73 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 4 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.81 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.843
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2013 | ClimateZone 4 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092
90.1-2013 | ClimateZone 4 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 4 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.430_in |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Glass with Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.15 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Plastic with Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.15 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 4 |  | Skylight | Without Curb | Semiheated | U 1.15 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.15 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.082 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.055 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.055 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.62 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.62 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2013 | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092
90.1-2013 | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.430_in |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36
90.1-2013 | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.34
90.1-2013 | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27
90.1-2013 | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.087 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.031 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.029 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.06 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.049 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.049 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/6mm Air |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  |  |  | 0.51 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.4 | 1.1
90.1-2013 | ClimateZone 6 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.59 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.671
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092
90.1-2013 | ClimateZone 6 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.063
90.1-2013 | ClimateZone 6 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2013 | ClimateZone 6 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.430_in |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 6 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36
90.1-2013 | ClimateZone 6 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 6 |  | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 6 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 6 |  | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE |  |  | 0.39
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.042 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.042 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.27 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.074 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.029 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.029 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.044 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.049 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.044 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.042 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.072 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.40 SHGC 0.45 |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  |  |  | 0.44 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.671
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.671
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.063
90.1-2013 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.063
90.1-2013 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2013 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.334_in |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.27
90.1-2013 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.27
90.1-2013 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36
90.1-2013 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19
90.1-2013 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.038 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.026 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.026 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.048 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.048 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.039 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.037 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.032 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.06 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.38 SHGC 0.30 Dbl Ref-B-H Clr 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.40 SHGC 0.45 |  |  |  | 0.77 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.68 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.30 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Air |  |  |  | 0.32 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.38 SHGC 0.26 Dbl Ref B-H Tint 6mm/13mm Arg |  |  |  | 0.38 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.40 SHGC 0.43 Dbl LoE Spec Sel Clr 3mm/6mm/6mm Air |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.45 | 1.1
90.1-2013 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.44 SHGC 0.20 Dbl Ref-B-H Tint 6mm/13mm Air |  |  |  | 0.44 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.671
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.424
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.373
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.86
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.063
90.1-2013 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.063
90.1-2013 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
90.1-2013 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.50_SHGC_0.40_Skylight_Frame_Width_0.000_in |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.39
90.1-2013 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36
90.1-2013 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.65
90.1-2013 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE |  |  | 0.27
90.1-2013 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE
90.1-2013 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.85 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.85 | TRUE | TRUE |  |  | 0.39
90.1-2013 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 1151 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.44 SHGC 0.26 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.5 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 0.93 | TRUE | TRUE |  |  | 0.25
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2013 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.1 | TRUE | TRUE |  |  | 0.25
90.1-2013 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.65 SHGC 0.25 Dbl Ref-C-H Clr 6mm/6mm Air |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.25 | 1.1
90.1-2013 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  | 1.2 | TRUE | TRUE |  |  | 0.25
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
90.1-2013 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | Window_U_0.75_SHGC_0.35_Skylight_Frame_Width_2.339_in |  | 0 | 2 | 0.75 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.75 | TRUE | TRUE |  |  | 0.49
90.1-2013 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE |  |  | 0.49
90.1-2013 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 0.75 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.75 | TRUE | TRUE |  |  | 0.39
90.1-2013 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.75 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE
90.1-2013 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 0.75 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.75 | TRUE | TRUE |  |  | 0.68
90.1-2013 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 0.75 SHGC 0.35 Simple Glazing Skylight |  | 0 | 2 | 0.75 | TRUE | TRUE |  |  | 0.64
90.1-2013 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.80 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.8 | TRUE | TRUE |  |  | 0.64
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.074 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.074 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.614 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.34 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.15 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.39 Sgl Ref-B-H Clr 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.046 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.046 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.41 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.24 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 2B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.29 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.25 Simple Glazing Window |  |  |  | 0.72 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.143 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.143 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.34
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 3A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.048 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.048 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.29 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.16 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.088 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.088 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.49 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.13 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.39 Simple Glazing Window |  |  |  | 0.72 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.143 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.143 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.61 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 3C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.086 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.086 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.12 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.36 Simple Glazing Window |  |  |  | 0.59 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.111 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.111 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.059 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.059 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.19 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.36 Simple Glazing Window |  |  |  | 0.72 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.064 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.064 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.085 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.085 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.092 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.72 SHGC 0.39 Simple Glazing Window |  |  |  | 0.72 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.111 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.111 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 4C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  |  | 0.59 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.14 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  |  | 0.59 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.14 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.082 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.59 SHGC 0.39 Simple Glazing Window |  |  |  | 0.59 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 5C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.0066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.39 Simple Glazing Window |  |  |  | 0.52 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.083 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.083 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.34
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 6A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.0066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.049 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.049 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.079 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.072 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.39 Simple Glazing Window |  |  |  | 0.52 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.091 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.091 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.34
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.61
DOE Ref 1980-2004 | ClimateZone 6B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.04 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.04 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.04 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.04 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.061 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.058 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.49 Simple Glazing Window |  |  |  | 0.52 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.077 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.077 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.031 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.031 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.031 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.031 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.047 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.045 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.52 SHGC 0.615 Simple Glazing Window |  |  |  | 0.52 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0.063 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0.063 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.49
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.36
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.81 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 1 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.25 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref 1980-2004 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.16
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.34
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.27
DOE Ref 1980-2004 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 1.45 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.614 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.35 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 2B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 2B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.225 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.34
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 3A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.282 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.224 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.61 Sgl Green 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 3C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.61 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 3C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.086 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.086 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.086 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.178 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.184 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.085 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.085 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.085 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.081 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.175 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 4C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Plastic with Curb | Nonresidential | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Plastic with Curb | Residential | U 1.30 SHGC 0.62 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Without Curb | Residential | U 0.58 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 4C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.072 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.072 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.072 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.156 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.7 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.076 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.161 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 5C |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Plastic with Curb | Nonresidential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Plastic with Curb | Residential | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 5C |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.0066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6A |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.34
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 6A |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.322 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.069 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.0066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.145 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 6B |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.71 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Plastic with Curb | Residential | U 0.74 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.74 | TRUE | TRUE |  |  | 0.34
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.49 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.61
DOE Ref Pre-1980 | ClimateZone 6B |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.066 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.053 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.065 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.136 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  |  |  | 0.57 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.84
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Glass with Curb | Residential | U 1.17 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 1.17 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Plastic with Curb | Nonresidential | U 0.87 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.87 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Without Curb | Nonresidential | U 0.69 SHGC 0.68 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Without Curb | Residential | U 0.69 SHGC 0.64 Simple Glazing Skylight |  | 0 | 2 | 0.69 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 7 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.65
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.5 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.137 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.032 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.06 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.049 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.125 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.057 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.124 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.62 SHGC 0.41 Simple Glazing Window |  |  |  | 0.62 | TRUE | TRUE |  |  | 0.41
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.46 SHGC 0.45 Dbl Grey 6mm/13mm Air |  |  |  | 0.46 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.78
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.95
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Glass with Curb | Residential | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Glass with Curb | Semiheated | U 1.30 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 1.3 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Plastic with Curb | Nonresidential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Plastic with Curb | Residential | U 0.61 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 0.61 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Plastic with Curb | Semiheated | U 1.10 SHGC 0.77 Simple Glazing Skylight |  | 0 | 2 | 1.1 | TRUE | TRUE |  |  | 0.36
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Without Curb | Nonresidential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE |  |  | 0.19
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Without Curb | Residential | U 0.57 SHGC 0.49 Dbl Blue 6mm/6mm Air |  | 0 | 2 | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 8 |  | Skylight | Without Curb | Semiheated | U 0.81 SHGC 0.65 Simple Glazing Skylight |  | 0 | 2 | 0.81 | TRUE | TRUE
ECBC 2007 | ECBC Composite | 24 Hour | ExteriorWall |  | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.2 | TRUE | TRUE
ECBC 2007 | ECBC Composite | Daytime | ExteriorWall |  | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.1 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential |  |  |  |  | 0.4 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorFloor | Mass | Residential |  |  |  |  | 0.064 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.03 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.165 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE
ICC IECC 2015 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential |  |  |  |  | 0.4 | TRUE | TRUE |  |  | 0.25
ICC IECC 2015 | ClimateZone 2 |  | Skylight | Glass with Curb | Residential |  |  |  |  | 0.65 | TRUE | TRUE |  |  | 0.3
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.23 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.58 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.113 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.352 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.292 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 1.22 SHGC 0.54 Simple Glazing Window |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.54
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.88 SHGC 0.16 Sgl Ref-A-L Clr 6mm |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Residential | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE |  |  | 0.25
DOE Ref Pre-1980 | ClimateZone 1 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 1.22 SHGC 0.25 Sgl Elec Ref Colored 6mm |  |  |  | 1.22 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Mass | Nonresidential | ext-slab-mass |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | SteelFramed | Nonresidential | ext-slab-steel-frame |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Metal Building | Nonresidential | ext-slab-metal-building |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Unheated | Semiheated | ext-slab |  |  |  |  | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 1.02
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  | 0 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Glass with Curb | Nonresidential | [5 empty] | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Glass with Curb | Residential | U 1.98 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.49
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Glass with Curb | Semiheated | U 1.98 SHGC 0.36 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 1.98 | TRUE | TRUE |  |  | 0.39
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Plastic with Curb | Nonresidential | U 1.90 SHGC 0.34 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Plastic with Curb | Residential | U 1.90 SHGC 0.27 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Plastic with Curb | Semiheated | U 1.90 SHGC 0.39 Simple Glazing Skylight |  | 0 | 2 | 1.9 | TRUE | TRUE |  |  | 0.77
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Without Curb | Nonresidential | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.77
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Without Curb | Residential | U 1.36 SHGC 0.19 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE |  |  | 0.62
DOE Ref Pre-1980 | ClimateZone 1 |  | Skylight | Without Curb | Semiheated | U 1.36 SHGC 0.36 Simple Glazing Skylight |  | 0 | 2 | 1.36 | TRUE | TRUE
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.45 SHGC 0.25 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.25 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.60 SHGC 0.23 Simple Glazing Window |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.45 SHGC 0.25 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.25 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.60 SHGC 0.23 Simple Glazing Window |  |  |  | 0.6 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.123 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.42 SHGC 0.25 Simple Glazing Window |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.25 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.54 SHGC 0.23 Simple Glazing Window |  |  |  | 0.54 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.42 SHGC 0.25 Simple Glazing Window |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.25 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.54 SHGC 0.23 Simple Glazing Window |  |  |  | 0.54 | TRUE | TRUE |  |  | 0.23 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.104 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.9 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.064 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.36 SHGC 0.36 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.33 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.33 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.36 SHGC 0.36 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.33 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.33 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | Swinging | Semiheated | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Semiheated | Typical Overhead Door |  |  |  | 0.36 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | IEAD | Semiheated | Typical IEAD Roof |  |  |  | 0.063 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Nonresidential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Residential | Typical Insulated Metal Building Roof |  |  |  | 0.037 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Metal Building | Semiheated | Typical Insulated Metal Building Roof |  |  |  | 0.082 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Semiheated | Typical Wood Joist Attic Floor |  |  |  | 0.034 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Metal Building | Nonresidential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.055 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Metal Building | Residential | Typical Insulated Metal Building Wall |  |  |  | 0.05 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.055 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Mass | Semiheated | Typical Insulated Exterior Mass Wall |  |  |  | 0.151 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Metal Building | Semiheated | Typical Insulated Metal Building Wall |  |  |  | 0.094 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Wall |  |  |  | 0.084 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.089 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.09 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.8 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Nonresidential | U 0.25 SHGC 0.40 Dbl LoE (e2-.1) Tint 6mm/13mm Arg |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.4 | 1.1 | Lower U windows than 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Residential | U 0.29 SHGC 0.22 Trp LoE Film (55) Bronze 6mm/6mm Air |  |  |  | 0.29 | TRUE | TRUE |  |  | 0.22 | 1.1 | Lower U and SHGC windows than 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Nonmetal framing (all) | Semiheated | U 0.45 SHGC 0.31 Dbl Ref-B-H Clr 6mm/13mm Air |  |  |  | 0.45 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Semiheated | U 0.62 SHGC 0.39 Dbl Ref-D Clr 6mm/6mm Air |  |  |  | 0.62 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Semiheated | U 0.72 SHGC 0.25 Sgl Ref-B-M Tint 6mm |  |  |  | 0.77 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.36 SHGC 0.38 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.38 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.45 SHGC 0.33 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.33 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.36 SHGC 0.38 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.38 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.45 SHGC 0.33 Simple Glazing Window |  |  |  | 0.45 | TRUE | TRUE |  |  | 0.33 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.4 | 1.1 | Lower U windows than 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.29 SHGC 0.22 Trp LoE Film (55) Bronze 6mm/6mm Air |  |  |  | 0.29 | TRUE | TRUE |  |  | 0.22 | 1.1 | Lower U and SHGC windows than 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm |  |  |  | 0.7 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Heated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Heated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.688 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Unheated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Heated | Semiheated | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.9 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.52 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119 |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092 |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14 |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36 |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19 |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.34 |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27 |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36 |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.08 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.34 SHGC 0.38 Simple Glazing Window |  |  |  | 0.34 | TRUE | TRUE |  |  | 0.38 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.42 SHGC 0.34 Simple Glazing Window |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.34 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.34 SHGC 0.38 Simple Glazing Window |  |  |  | 0.34 | TRUE | TRUE |  |  | 0.38 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.42 SHGC 0.34 Simple Glazing Window |  |  |  | 0.42 | TRUE | TRUE |  |  | 0.34 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.071 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.29 SHGC 0.40 Simple Glazing Window |  |  |  | 0.29 | TRUE | TRUE |  |  | 0.4 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.36 SHGC 0.36 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.29 SHGC 0.40 Simple Glazing Window |  |  |  | 0.29 | TRUE | TRUE |  |  | 0.4 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.36 SHGC 0.36 Simple Glazing Window |  |  |  | 0.36 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.51 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.37 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.028 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.048 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.048 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.032 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.26 SHGC 0.40 Simple Glazing Window |  |  |  | 0.26 | TRUE | TRUE |  |  | 0.4 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.32 SHGC 0.36 Simple Glazing Window |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.26 SHGC 0.40 Simple Glazing Window |  |  |  | 0.26 | TRUE | TRUE |  |  | 0.4 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.32 SHGC 0.36 Simple Glazing Window |  |  |  | 0.32 | TRUE | TRUE |  |  | 0.36 | 1.1 | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.424 |  |  |  | Same as 90.1-2019
NREL ZNE Ready 2017 | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.48 SHGC 0.21 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.21 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.19 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.19 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.48 SHGC 0.22 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.48 SHGC 0.20 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.2 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 0 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 0 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.039 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.04 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.48 SHGC 0.22 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.48 SHGC 0.20 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.2 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.48 SHGC 0.22 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.48 SHGC 0.20 Simple Glazing Window |  |  |  | 0.48 | TRUE | TRUE |  |  | 0.2 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 1 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 1 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.35 SHGC 0.24 Simple Glazing Window |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.24 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.35 SHGC 0.22 Simple Glazing Window |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.35 SHGC 0.24 Simple Glazing Window |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.24 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.35 SHGC 0.22 Simple Glazing Window |  |  |  | 0.35 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 2 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 2 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.73 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 2 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.027 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.029 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.25 SHGC 0.24 Simple Glazing Window |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.24 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.25 SHGC 0.22 Simple Glazing Window |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.25 SHGC 0.24 Simple Glazing Window |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.24 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.25 SHGC 0.22 Simple Glazing Window |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.22 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 3 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 3 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.54 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 3 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.021 | TRUE | TRUE |  |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.025 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.025 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.025 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.025 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.23 SHGC 0.34 Simple Glazing Window |  |  |  | 0.23 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.23 SHGC 0.31 Simple Glazing Window |  |  |  | 0.23 | TRUE | TRUE |  |  | 0.31 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.23 SHGC 0.34 Simple Glazing Window |  |  |  | 0.23 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.23 SHGC 0.31 Simple Glazing Window |  |  |  | 0.23 | TRUE | TRUE |  |  | 0.31 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.494 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.494 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 4 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | Mass | Nonresidential | Typical Insulated Exterior Mass Floor |  |  |  | 0.057 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Nonresidential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | Mass | Residential | Typical Insulated Exterior Mass Floor |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Residential | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.038 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.033 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | Mass | Semiheated | Typical Insulated Exterior Mass Floor |  |  |  | 0.107 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | SteelFramed | Semiheated | Typical Insulated Steel Framed Exterior Floor |  |  |  | 0.052 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | WoodFramed | Semiheated | Typical Insulated Wood Framed Exterior Floor |  |  |  | 0.051 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.022 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.17 SHGC 0.36 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.36 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.17 SHGC 0.31 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.31 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.17 SHGC 0.36 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.36 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.17 SHGC 0.31 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.31 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Nonresidential | U 0.60 SHGC 0.25 Dbl 2.5mm air |  |  |  | 0.25 | TRUE | TRUE |  |  | 0.4 | 1.1 | Lower U windows than 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Residential | U 0.29 SHGC 0.22 Trp LoE Film (55) Bronze 6mm/6mm Air |  |  |  | 0.29 | TRUE | TRUE |  |  | 0.22 | 1.1 | Lower U and SHGC windows than 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | GlassDoor | Metal framing (entrance door) | Semiheated | U 0.67 SHGC 0.77 Sgl LoE (e2-.2) Clr 3mm |  |  |  | 0.7 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.494 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.494 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactWall | Mass | Nonresidential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.119 |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactWall | Mass | Residential | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 0.092 |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | GroundContactWall | Mass | Semiheated | Typical Insulated Basement Mass Wall |  |  |  |  | TRUE | TRUE |  | 1.14 |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Glass with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.36 |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Glass with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.19 |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Glass with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Plastic with Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Plastic with Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  | 0.34 |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Plastic with Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.27 |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Without Curb | Nonresidential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Without Curb | Residential | U 0.48 SHGC 0.40 Dbl Ref-D Clr 6mm/13mm |  | 0 | 2 | 0.5 | TRUE | TRUE |  |  |  |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 5 |  | Skylight | Without Curb | Semiheated | U 0.98 SHGC 0.45 Sgl Ref-B-H Clr 6mm |  | 0 | 2 | 0.98 | TRUE | TRUE |  |  | 0.36 |  | Same as 90.1-2013
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.018 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.17 SHGC 0.36 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.36 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.17 SHGC 0.32 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.32 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.17 SHGC 0.36 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.36 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.17 SHGC 0.32 Simple Glazing Window |  |  |  | 0.17 | TRUE | TRUE |  |  | 0.32 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 6 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 6 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.434 |  |  |  | Same as 90.1-2019
ZE AEDG Multifamily | ClimateZone 6 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.14 SHGC 0.38 Simple Glazing Window |  |  |  | 0.14 | TRUE | TRUE |  |  | 0.38 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.14 SHGC 0.34 Simple Glazing Window |  |  |  | 0.14 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.14 SHGC 0.38 Simple Glazing Window |  |  |  | 0.14 | TRUE | TRUE |  |  | 0.38 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.14 SHGC 0.34 Simple Glazing Window |  |  |  | 0.14 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.4 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.4 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 7 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorDoor | Swinging | Nonresidential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Nonresidential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorDoor | Swinging | Residential | Typical Insulated Metal Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorDoor | NonSwinging | Residential | Typical Overhead Door |  |  |  | 0.2 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorFloor | Mass | Adiabatic | Adiabatic ExteriorFloor |  |  | 0
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorRoof | IEAD | Nonresidential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorRoof | IEAD | Residential | Typical IEAD Roof |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Nonresidential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Residential | Typical Wood Joist Attic Floor |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorRoof | Attic and Other | Adiabatic | Adiabatic Roof |  |  | 0
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWall | Mass | Nonresidential | Typical Insulated Exterior Mass Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWall | WoodFramed | Nonresidential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWall | Mass | Residential | Typical Insulated Exterior Mass Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWall | WoodFramed | Residential | Typical Insulated Wood Framed Exterior Wall |  |  |  | 0.017 | TRUE | TRUE |  |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWall | Mass | Adiabatic | Adiabatic Wall |  |  | 0
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Nonresidential | U 0.12 SHGC 0.38 Simple Glazing Window |  |  |  | 0.12 | TRUE | TRUE |  |  | 0.38 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Nonresidential | U 0.12 SHGC 0.34 Simple Glazing Window |  |  |  | 0.12 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWindow | Metal framing (curtainwall/storefront) | Residential | U 0.12 SHGC 0.38 Simple Glazing Window |  |  |  | 0.12 | TRUE | TRUE |  |  | 0.38 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | ExteriorWindow | Metal framing (all other) | Residential | U 0.12 SHGC 0.34 Simple Glazing Window |  |  |  | 0.12 | TRUE | TRUE |  |  | 0.34 | 1.1 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | GroundContactFloor | Unheated | Nonresidential | Typical Insulated Carpeted 8in Slab Floor |  |  |  |  | TRUE | TRUE | 0.4 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | GroundContactFloor | Unheated | Residential | Typical Insulated Carpeted 6in Slab Floor |  |  |  |  | TRUE | TRUE | 0.4 |  |  |  | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | ClimateZone 8 |  | GroundContactFloor | Mass | Adiabatic | Adiabatic GroundContactFloor |  |  | 0

## Window Types and Weights
| ASHRAE 90.1-2004 |  | ASHRAE 90.1-2007 2010 2013 2016 |  |  |  | 90.1-2004
| Fixed | Operable (not including entrance doors) | Nonmetal | Metal Curtainwall / Storefront | Metal Entrance Door | Metal - all other | U | SHGC
SmallOffice | 95.44% | 4.56% | 1.63% | 62.22% | Not Included | 36.23%
MediumOffice | 95.44% | 4.56% | 1.63% | 62.22% | Not Included | 36.23%
LargeOffice | 100% | 0% | 1.63% | 62.22% | Not Included | 36.23%
RetailStandalone | 98.45% | 1.55% | 9.93% | 62.41% | Not Included | 28.36%
RetailStripmall | 98.45% | 1.55% | 9.93% | 62.41% | Not Included | 28.36%
PrimarySchool | 98.45% | 1.55% | 9.93% | 62.41% | Not Included | 28.36%
SecondarySchool | 98.45% | 1.55% | 9.93% | 62.41% | Not Included | 28.36%
Outpatient | 94.54% | 5.46% | 2.02% | 9.87% | Not Included | 88.21%
Hospital | 65.21% | 34.56% | 21.61% | 44.55% | Not Included | 33.81%
SmallHotel | 65.21% | 34.56% | 21.61% | 44.55% | Not Included | 33.81%
LargeHotel | 87.71% | 12.29% | 9% | 60.1% | Not Included | 31.1%
Warehouse | 87.71% | 12.29% | 9% | 60.1% | Not Included | 31.1%
QuickServiceRestaurant | 78.34% | 21.66% | 11.5% | 20.52% | Not Included | 68.06%
FullServiceRestaurant | 78.34% | 21.66% | 11.5% | 20.52% | Not Included | 68.06%
MidriseApartment | 41.73% | 58.27% | 31.91% | 4.99% | Not Included | 63.13%
HighriseApartment | 41.73% | 58.27% | 31.91% | 4.99% | Not Included | 63.13%
Courthouse | 100% | 0% | 0% | 0% | Not Included | 100%
SmallDataCenterLowITE | 100% | 0% | 0% | 0% | Not Included | 100%
SmallDataCenterHighITE | 100% | 0% | 0% | 0% | Not Included | 100%
LargeDataCenterLowITE | 100% | 0% | 0% | 0% | Not Included | 100%
LargeDataCenterHighITE | 100% | 0% | 0% | 0% | Not Included | 100%
College | 100% | 35% | 0% | 0% | Not Included | 100%

## Boilers
Each row represents the efficiency standards for a specific type of boiler
Template | Fluid Type | Fuel Type | Condensing | Condensing Control | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Annual Fuel Utilization Efficiency (AFUE) | Minimum Thermal Efficiency (%) | Minimum Combustion Efficiency (%) | EFFFPLR | Notes
DOE Ref Pre-1980 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 |  | 0.73 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas |  |  | 300000 | 9999999999 | 1919-09-09 | 401655 |  | 0.74 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref Pre-1980 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  | 0.76 |  | Boiler Constant Efficiency Curve | From DOE Reference Buildings
DOE Ref 1980-2004 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler Constant Efficiency Curve | From 90.1-1989
DOE Ref 1980-2004 | Hot Water | Gas |  |  | 300000 | 249999999 | 1919-09-09 | 401655 |  |  | 0.8 | Boiler Constant Efficiency Curve | From 90.1-1989
90.1-2004 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas |  |  | 300000 | 249999999 | 1919-09-09 | 401655 |  | 0.75 |  | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2004 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.8 | Boiler with No Minimum Turndown | From 90.1-2004
90.1-2007 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas |  |  | 300000 | 249999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2007 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2007
90.1-2010 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas |  |  | 300000 | 249999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2010 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.82 | Boiler with No Minimum Turndown | From 90.1-2010
90.1-2013 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas |  |  | 300000 | 999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas |  |  | 1000000 | 249999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with Minimum Turndown | From 90.1-2013
90.1-2013 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.82 | Boiler with Minimum Turndown | From 90.1-2013
OEESC 2014 | Hot Water | Gas |  |  | 0 | 299999 | 1919-09-09 | 401655 | 0.8 |  |  | Boiler with No Minimum Turndown | From 90.1-2013
OEESC 2014 | Hot Water | Gas |  |  | 300000 | 999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with No Minimum Turndown | From 90.1-2013
OEESC 2014 | Hot Water | Gas |  |  | 1000000 | 249999999 | 1919-09-09 | 401655 |  | 0.8 |  | Boiler with Minimum Turndown | From 90.1-2013
OEESC 2014 | Hot Water | Gas |  |  | 250000000 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.82 | Boiler with Minimum Turndown | From 90.1-2013
NREL ZNE Ready 2017 | Hot Water | Gas |  |  | 0 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.94 | Boiler with Minimum Turndown | Assumes a condensing boiler
ZE AEDG Multifamily | Hot Water | Gas |  |  | 0 | 9999999999 | 1919-09-09 | 401655 |  |  | 0.94 | Boiler with Minimum Turndown | Assumes a condensing boiler

## Chillers
Each row represents the efficiency standards for a specificy type of chiller
Template | Cooling Type | Condenser Type | Compressor Type | Absorption Type | Variable Speed Drive | Minimum Capacity (Tons) | Maximum Capacity (Tons) | Start Date | End Date | Minimum Full Load Efficiency (kW/ton) | Minimum Integrated Part Load Value (kW/ton) | CAPFT | EIRFT | EIRFPLR | Notes
90.1-2004 | AirCooled | WithCondenser |  |  |  | 0 | 9999 | 1919-09-09 | 401655 | 1.256 | 1.153 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2004 | AirCooled | WithoutCondenser |  |  |  | 0 | 9999 | 1919-09-09 | 401655 | 1.135 | 1.019 | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio
90.1-2004 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.862
90.1-2007 | AirCooled | WithCondenser |  |  |  | 0 | 9999 | 1919-09-09 | 401655 | 1.29 | 1.164 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Form 90.1-2007 Table 6.8.1A
90.1-2010 | AirCooled | WithCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 401655 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled | WithoutCondenser |  |  |  | 0 | 9999 | 1919-09-09 | 401655 | 1.255 | 0.941 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
90.1-2010 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.862
90.1-2013 | AirCooled | WithCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 2014-12-31 | 1.25 | 0.96 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Path A Efficiencies
90.1-2013 | AirCooled | WithCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 2014-12-31 | 1.25 | 0.94 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Path A Efficiencies
90.1-2013 | AirCooled | WithoutCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 2014-12-31 | 1.25 | 0.96 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | AirCooled | WithoutCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 2014-12-31 | 1.25 | 0.94 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 2014-12-31 | 5.862 |  |  |  |  | Path A Efficiencies
90.1-2013 | AirCooled | WithCondenser |  |  |  | 0 | 149.99 | 2015-01-01 | 2014-12-31 | 1.188 | 0.876 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Path A Efficiencies
90.1-2013 | AirCooled | WithCondenser |  |  |  | 150 | 9999 | 2015-01-01 | 401655 | 1.188 | 0.857 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Path A Efficiencies
90.1-2013 | AirCooled | WithoutCondenser |  |  |  | 0 | 149.99 | 2015-01-01 | 401655 | 1.188 | 0.876 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | AirCooled | WithoutCondenser |  |  |  | 150 | 9999 | 2015-01-01 | 401655 | 1.188 | 0.857 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 2015-01-01 | 401655 | 5.862 |  |  |  |  | Path A Efficiencies
DOE Ref 1980-2004 | AirCooled | WithCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 401655 | 1.407 | 1.407 | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | WithoutCondenser |  |  |  | 0 | 9999 | 1919-09-09 | 401655 | 1.135 | 1.099 | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From 90.1-1989
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.303 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 1.332 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithCondenser |  |  |  | 300 | 9999 | 1919-09-09 | 401655 | 1.332 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.303 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 1.332 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled | WithoutCondenser |  |  |  | 300 | 9999 | 1919-09-09 | 401655 | 1.332 |  | ChlrAirRecipQRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fTchwsToadbSI | ChlrAirRecipEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 6.395 |  | ChlrAirRecipQRatio_fTchwsToadbSI |  |  | From DOE Reference Buildings
OEESC 2014 | AirCooled | WithCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.188 | 0.876 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
OEESC 2014 | AirCooled | WithCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 401655 | 1.188 | 0.857 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR
OEESC 2014 | AirCooled | WithoutCondenser |  |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.188 | 0.876 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio
OEESC 2014 | AirCooled | WithoutCondenser |  |  |  | 150 | 9999 | 1919-09-09 | 401655 | 1.188 | 0.857 | ChlrAirScrollQRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fTchwsToadbSI | ChlrAirScrollEIRRatio_fQRatio
OEESC 2014 | AirCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.862
NREL ZNE Ready 2017 | AirCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.0695 | 0.77922 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | from ASHRAE 189.1-2017
NREL ZNE Ready 2017 | AirCooled |  | Rotary Screw |  |  | 140 | 9999 | 1919-09-09 | 401655 | 1 | 0.76433 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | from ASHRAE 189.1-2017
90.1-2004 | WaterCooled |  | Reciprocating |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.837 | 0.696 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Reciprocating |  |  | 150 | 9999 | 1919-09-09 | 401655 | 0.837 | 0.696 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.79 | 0.676 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.718 | 0.628 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Rotary Screw |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.639 | 0.572 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Scroll |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.79 | 0.676 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.718 | 0.628 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Scroll |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.639 | 0.572 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.634 | 0.596 | WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.703 | 0.67 | WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  | Centrifugal |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.577 | 0.55 | WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
90.1-2004 | WaterCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.024
90.1-2007 | WaterCooled |  | Reciprocating |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Reciprocating |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Reciprocating |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Scroll |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Scroll |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Scroll |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Rotary Screw |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Rotary Screw |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Rotary Screw |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.634 | 0.596 | WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.634 | 0.596 | WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Centrifugal |  |  | 300 | 599.99 | 1919-09-09 | 401655 | 0.576 | 0.549 | WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2007 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.57 | 0.539 | WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Reciprocating |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Scroll |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.78 | 0.63 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.775 | 0.615 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.68 | 0.58 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Rotary Screw |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.62 | 0.54 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.634 | 0.596 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.634 | 0.596 | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  |  | 300 | 599.99 | 1919-09-09 | 401655 | 0.576 | 0.549 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.57 | 0.539 | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Minimum Efficiencies
90.1-2010 | WaterCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.024
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 0 | 74.99 | 1919-09-09 | 2014-12-31 | 0.78 | 0.63 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 75 | 149.99 | 1919-09-09 | 2014-12-31 | 0.775 | 0.615 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 2014-12-31 | 0.68 | 0.58 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 300 | 599.99 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 600 | 9999 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 0 | 74.99 | 1919-09-09 | 2014-12-31 | 0.78 | 0.63 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 75 | 149.99 | 1919-09-09 | 2014-12-31 | 0.775 | 0.615 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 2014-12-31 | 0.68 | 0.58 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 300 | 599.99 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 600 | 9999 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 0 | 74.99 | 1919-09-09 | 2014-12-31 | 0.78 | 0.63 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 75 | 149.99 | 1919-09-09 | 2014-12-31 | 0.775 | 0.615 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 2014-12-31 | 0.68 | 0.58 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 300 | 599.99 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 600 | 9999 | 1919-09-09 | 2014-12-31 | 0.62 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 2014-12-31 | 0.634 | 0.596 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 300 | 399.99 | 1919-09-09 | 2014-12-31 | 0.634 | 0.596 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 400 | 599.99 | 1919-09-09 | 2014-12-31 | 0.576 | 0.549 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 2014-12-31 | 0.57 | 0.539 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Add but unsure what to put for Minimum full load efficiency and min IPLV
90.1-2013 | WaterCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.024 |  |  |  |  | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 0 | 74.99 | 2015-01-01 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 75 | 149.99 | 2015-01-01 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 2015-01-01 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 300 | 599.99 | 2015-01-01 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Reciprocating |  |  | 600 | 9999 | 2015-01-01 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 0 | 74.99 | 2015-01-01 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 75 | 149.99 | 2015-01-01 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 2015-01-01 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 300 | 599.99 | 2015-01-01 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Scroll |  |  | 600 | 9999 | 2015-01-01 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 0 | 74.99 | 2015-01-01 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 75 | 149.99 | 2015-01-01 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 2015-01-01 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 300 | 599.99 | 2015-01-01 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Rotary Screw |  |  | 600 | 9999 | 2015-01-01 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 2015-01-01 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 300 | 399.99 | 2015-01-01 | 401655 | 0.56 | 0.52 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 400 | 599.99 | 2015-01-01 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Path A Efficiencies
90.1-2013 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 2015-01-01 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | Add but unsure what to put for Minimum full load efficiency and min IPLV
NREL ZNE Ready 2017 | WaterCooled |  | Reciprocating |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Reciprocating |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Reciprocating |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Reciprocating |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Scroll |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Scroll |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Scroll |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Scroll |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Rotary Screw |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Rotary Screw |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Rotary Screw |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Centrifugal |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.56 | 0.52 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Centrifugal |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
NREL ZNE Ready 2017 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.926 | 0.902 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.837 | 0.782 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Reciprocating |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.676 | 0.664 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.926 | 0.902 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.837 | 0.782 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Rotary Screw |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.676 | 0.664 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.926 | 0.902 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.837 | 0.782 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Scroll |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.676 | 0.664 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.926 | 0.902 | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.837 | 0.782 | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref 1980-2004 | WaterCooled |  | Centrifugal |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.676 | 0.664 | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-1989
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.884 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.884 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Reciprocating |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.884 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.852 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.782 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Rotary Screw |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.688 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.852 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.782 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Scroll |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.688 |  | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.776 |  | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.713 |  | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  | Centrifugal |  |  | 300 | 9999 | 1919-09-09 | 401655 | 0.635 |  | ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrCentPathAAllEIRRatio_fQRatio | From DOE Reference Buildings
DOE Ref Pre-1980 | WaterCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.097 |  |  |  |  | From DOE Reference Buildings
OEESC 2014 | WaterCooled |  | Reciprocating |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Reciprocating |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Reciprocating |  |  | 300 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Reciprocating |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Scroll |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Scroll |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Scroll |  |  | 300 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Scroll |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Rotary Screw |  |  | 0 | 74.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Rotary Screw |  |  | 75 | 149.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Rotary Screw |  |  | 300 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Rotary Screw |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Centrifugal |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.56 | 0.52 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Centrifugal |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio
OEESC 2014 | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio | Add but unsure what to put for Minimum full load efficiency and min IPLV
OEESC 2014 | WaterCooled |  |  | Single Effect |  | 0 | 9999 | 1919-09-09 | 401655 | 5.024
90.1-2004 |  |  |  | Double Effect Indirect Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.35
90.1-2004 |  |  |  | Double Effect Direct Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.517
90.1-2010 |  |  |  | Double Effect Indirect Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.35
90.1-2010 |  |  |  | Double Effect Direct Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.517
90.1-2013 |  |  |  | Double Effect Indirect Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.35 |  |  |  | Path A Efficiencies
90.1-2013 |  |  |  | Double Effect Direct Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.517 |  |  |  | Path A Efficiencies
DOE Ref Pre-1980 |  |  |  | Double Effect Indirect Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.589 |  |  |  |  | From DOE Reference Buildings
DOE Ref Pre-1980 |  |  |  | Double Effect Direct Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.589 |  |  |  |  | From DOE Reference Buildings
OEESC 2014 |  |  |  | Double Effect Indirect Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 3.35
OEESC 2014 |  |  |  | Double Effect Direct Fired |  | 0 | 9999 | 1919-09-09 | 401655 | 3.517 | 1.05
ZE AEDG Multifamily | AirCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 1.0695 | 0.77922 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | from ASHRAE 189.1-2017
ZE AEDG Multifamily | AirCooled |  | Rotary Screw |  |  | 140 | 9999 | 1919-09-09 | 401655 | 1 | 0.76433 | AirCooled_Chiller_2010_PathA_CAPFT | AirCooled_Chiller_2010_PathA_EIRFT | AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | from ASHRAE 189.1-2017
ZE AEDG Multifamily | WaterCooled |  | Reciprocating |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Reciprocating |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Reciprocating |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Reciprocating |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Reciprocating |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Scroll |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Scroll |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Scroll |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Scroll |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Scroll |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Rotary Screw |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.75 | 0.6 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Rotary Screw |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.72 | 0.56 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Rotary Screw |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.66 | 0.54 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Rotary Screw |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.61 | 0.52 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Rotary Screw |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | ChlrWtrPosDispPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Centrifugal |  |  | 0 | 149.99 | 1919-09-09 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Centrifugal |  |  | 150 | 299.99 | 1919-09-09 | 401655 | 0.61 | 0.55 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Centrifugal |  |  | 300 | 399.99 | 1919-09-09 | 401655 | 0.56 | 0.52 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Centrifugal |  |  | 400 | 599.99 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3
ZE AEDG Multifamily | WaterCooled |  | Centrifugal |  |  | 600 | 9999 | 1919-09-09 | 401655 | 0.56 | 0.5 | WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | ChlrWtrCentPathAAllEIRRatio_fQRatio | From 90.1-2016 Table 6.8.1-3

## Heat Rejection
Each row represents the efficiency standards for a specific type of heat rejection equipment
Template | Equipment Type | Fan Type | Start Date | End Date | Minimum Performance (gal/min*hp) | Notes
DOE Ref Pre-1980 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
DOE Ref Pre-1980 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
DOE Ref Pre-1980 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
DOE Ref Pre-1980 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
DOE Ref 1980-2004 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
DOE Ref 1980-2004 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
DOE Ref 1980-2004 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
DOE Ref 1980-2004 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
90.1-2004 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
90.1-2004 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
90.1-2004 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2004 Table 6.8.1G
90.1-2004 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2004 Table 6.8.1G
90.1-2007 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2007 Table 6.8.1G
90.1-2007 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2007 Table 6.8.1G
90.1-2007 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2007 Table 6.8.1G
90.1-2007 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2007 Table 6.8.1G
90.1-2010 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2010 Table 6.8.1 G
90.1-2010 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 38.2 | From 90.1-2010 Table 6.8.1 G
90.1-2010 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 7 | From 90.1-2010 Table 6.8.1 G
90.1-2010 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 14 | From 90.1-2010 Table 6.8.1 G
90.1-2013 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2013 Table 6.8.1-7
90.1-2013 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 40.2 | From 90.1-2013 Table 6.8.1-7
90.1-2013 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 7 | From 90.1-2013 Table 6.8.1-7
90.1-2013 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 14 | From 90.1-2013 Table 6.8.1-7
NREL ZNE Ready 2017 | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2016 Table 6.8.1.7
NREL ZNE Ready 2017 | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 40.2 | From 90.1-2016 Table 6.8.1.7
NREL ZNE Ready 2017 | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 7 | From 90.1-2016 Table 6.8.1.7
NREL ZNE Ready 2017 | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 16.1 | From 90.1-2016 Table 6.8.1.7
ZE AEDG Multifamily | Open Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 20 | From 90.1-2016 Table 6.8.1.7
ZE AEDG Multifamily | Open Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 40.2 | From 90.1-2016 Table 6.8.1.7
ZE AEDG Multifamily | Closed Cooling Tower | Centrifugal | 1919-09-09 | 401655 | 7 | From 90.1-2016 Table 6.8.1.7
ZE AEDG Multifamily | Closed Cooling Tower | Propeller or Axial | 1919-09-09 | 401655 | 20 | From ZE AEDG Multifamily Committee

## Water Source Heat Pumps
Each row represents the efficiency standards for a specific type of heat pump
Template | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Full Load Efficiency (EER) | Notes
DOE Ref Pre-1980 | 0 | 16999 | 1919-09-09 | 401655 | 11.2 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
DOE Ref Pre-1980 | 17000 | 64999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
DOE Ref Pre-1980 | 65000 | 134999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
DOE Ref 1980-2004 | 0 | 16999 | 1919-09-09 | 401655 | 11.2 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
DOE Ref 1980-2004 | 17000 | 64999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
DOE Ref 1980-2004 | 65000 | 134999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 since DOE Reference Buildings did not have any water source heat pumps
90.1-2004 | 0 | 16999 | 1919-09-09 | 401655 | 11.2 | From 90.1-2004 Table 6.8.1B
90.1-2004 | 17000 | 64999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 Table 6.8.1B
90.1-2004 | 65000 | 134999 | 1919-09-09 | 401655 | 12 | From 90.1-2004 Table 6.8.1B
90.1-2007 | 0 | 16999 | 1919-09-09 | 401655 | 11.2 | From 90.1-2007 Table 6.8.1B
90.1-2007 | 17000 | 64999 | 1919-09-09 | 401655 | 12 | From 90.1-2007 Table 6.8.1B
90.1-2007 | 65000 | 134999 | 1919-09-09 | 401655 | 12 | From 90.1-2007 Table 6.8.1B
90.1-2010 | 0 | 16999 | 1919-09-09 | 401655 | 11.2 | From 90.1-2010 Table 6.8.1B
90.1-2010 | 17000 | 64999 | 1919-09-09 | 401655 | 12 | From 90.1-2010 Table 6.8.1B
90.1-2010 | 65000 | 134999 | 1919-09-09 | 401655 | 12 | From 90.1-2010 Table 6.8.1B
90.1-2013 | 0 | 16999 | 1919-09-09 | 401655 | 12.2 | From 90.1-2013 Table 6.8.1-2
90.1-2013 | 17000 | 64999 | 1919-09-09 | 401655 | 13 | From 90.1-2013 Table 6.8.1-2
90.1-2013 | 65000 | 134999 | 1919-09-09 | 401655 | 13 | From 90.1-2013 Table 6.8.1-2
NREL ZNE Ready 2017 | 0 | 16999 | 1919-09-09 | 401655 | 12.2 | From 90.1-2016 Table 6.8.1-2
NREL ZNE Ready 2017 | 17000 | 64999 | 1919-09-09 | 401655 | 13 | From 90.1-2016 Table 6.8.1-2
NREL ZNE Ready 2017 | 65000 | 134999 | 1919-09-09 | 401655 | 13 | From 90.1-2016 Table 6.8.1-2
ZE AEDG Multifamily | 0 | 16999 | 1919-09-09 | 401655 | 18.2 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | 17000 | 64999 | 1919-09-09 | 401655 | 18.2 | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | 65000 | 134999 | 1919-09-09 | 401655 | 18.2 | From ZE AEDG Multifamily Committee

## Water Source Heat Pumps Heating
Each row represents the efficiency standards for a specific type of heat pump
Template | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Coefficient of Performance Heating (COP_68F) | Notes
DOE Ref Pre-1980 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2004 since no DOE Reference Buildings had water source heat pumps
DOE Ref 1980-2004 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2004 since no DOE Reference Buildings had heat pumps
90.1-2004 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2004 Table 6.8.1B
90.1-2007 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2007 Table 6.8.1B
90.1-2010 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2010 Table 6.8.1B
90.1-2013 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2013 Table 6.8.1-2
NREL ZNE Ready 2017 | 0 | 9999999 | 1919-09-09 | 401655 | 4.2 | From 90.1-2016 Table 6.8.1-2
ZE AEDG Multifamily | 0 | 9999999 | 1919-09-09 | 401655 | 5.4 | From ZE AEDG Multifamily Committee

## Heat Pumps
Each row represents the efficiency standards for a specific type of heat pump
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Seasonal Efficiency (SEER) | Minimum Full Load Efficiency (EER) | Minimum IPLV | Minimum Integrated Energy Efficiency Ratio (IEER) | PTHP_EER_Coefficient_1 | PTHP_EER_Coefficient_2 | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-1989 Table 10-4A
DOE Ref Pre-1980 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-1989 Table 10-4A
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-1989 Table 10-4A
DOE Ref 1980-2004 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-1989 Table 10-4A
90.1-2004 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1D
90.1-2004 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1D
90.1-2007 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1D
90.1-2007 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1D
90.1-2010 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1D Before 10/8/2012
90.1-2010 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.3 | 0.213 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1D Before 10/8/2012
90.1-2013 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 2015-12-31 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-4
90.1-2013 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 2015-12-31 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-4
90.1-2013 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 2016-01-01 | 401655 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-4
90.1-2013 | AirCooled | All Other | PTHP | 0 | 9999999 | 2016-01-01 | 401655 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-4
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 15.4 | 0.33 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
NREL ZNE Ready 2017 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 15.4 | 0.33 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 15.4 | 0.33 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 15.4 | 0.33 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
OEESC 2014 | AirCooled | Electric Resistance or None | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(3)
OEESC 2014 | AirCooled | All Other | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(3)
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 9.7 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 10.6 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 10.6 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 2015-01-01 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 2015-01-01 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2
90.1-2013 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 2016-01-01 | 401655 |  | 11 |  | 12.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 | 2016-01-01 | 401655 |  | 10.8 |  | 12 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.6 |  | 11.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.4 |  | 11.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 2016-01-01 | 401655 |  | 9.5 |  | 10.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 9999999 | 2016-01-01 | 401655 |  | 9.3 |  | 0.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | Electric Resistance or None | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | All Other | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Single Package | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | SmallDuctHighVelocity | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | SmallDuctHighVelocity | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | SmallDuctHighVelocity | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | SmallDuctHighVelocity | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 since DOE Reference Buildings did not have any heat pumps
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | SmallDuctHighVelocity | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | SmallDuctHighVelocity | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2004 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2004 Table 6.8.1B
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10.9 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 10.9 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.9 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.3 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.1 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 8.8 | 9 |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 2015-01-01 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | AirCooled | All Other | Split System | 0 | 64999 | 2015-01-01 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2015
90.1-2013 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2
90.1-2013 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2
90.1-2013 | SmallDuctHighVelocity | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | SmallDuctHighVelocity | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 2016-01-01 | 401655 |  | 11 |  | 12.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 | 2016-01-01 | 401655 |  | 10.8 |  | 12 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.6 |  | 11.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.4 |  | 11.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 2016-01-01 | 401655 |  | 9.5 |  | 10.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
90.1-2013 | AirCooled | All Other | Split System | 240000 | 9999999 | 2016-01-01 | 401655 |  | 9.3 |  | 0.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From 90.1-2010 Table 6.8.1-2 Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 14 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | Electric Resistance or None | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | All Other | Split System | 0 | 29999 | 1919-09-09 | 401655 | 12 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | SmallDuctHighVelocity | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | SmallDuctHighVelocity | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.6 |  | 10.7 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.4 |  | 10.5 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 9.3 |  | 9.4 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From OEESC 2014 Table 503.2.3(2) Before 1/1/2016
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 20 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
NREL ZNE Ready 2017 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 20 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 16 |  |  |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From Pena Station design guidelines assumptions
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 20 | [5 empty] | Minisplit-Cool-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Cool-EIR-fFF | Minisplit-Cool-PLF-fPLR | From ZE AEDG Multifamily Committee
NREL ZNE Ready 2017 | AirCooled | All Other | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 20 | [5 empty] | Minisplit-Cool-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Cool-EIR-fFF | Minisplit-Cool-PLF-fPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 20 | [5 empty] | Minisplit-Cool-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Cool-EIR-fFF | Minisplit-Cool-PLF-fPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | All Other | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 20 | [5 empty] | Minisplit-Cool-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Cool-EIR-fFF | Minisplit-Cool-PLF-fPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 20 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 20 | [5 empty] | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 13.1 |  | 15 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 13.1 |  | 15 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 |  | 14 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 |  | 14 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 11 |  | 14 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | All Other | Split System | 240000 | 9999999 | 1919-09-09 | 401655 |  | 11 |  | 14 |  |  | HPACCoolCapFT | HPACCoolCapFFF | HPACCOOLEIRFT | HPACCOOLEIRFFF | HPACCOOLPLFFPLR | From ZE AEDG Multifamily Committee

## Heat Pumps Heating
Each row represents the efficiency standards for a specific type of heat pump
Template | Cooling Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Heating Seasonal Performance Factor | Minimum Coefficient of Performance Heating (COP_47F) | Minimum Energy Efficiency Ratio (EER) | PTHP_COP_Coefficient_1 | PTHP_COP_Coefficient_2 | HEAT CAP FT | HEAT CAP FFLOW | HEAT EIR FT | HEAT EIR FFLOW | HEAT PLF FPLR | Notes
DOE Ref Pre-1980 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 2.9 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-1989 Table 10-4A
DOE Ref 1980-2004 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 2.9 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-1989 Table 10-4A
90.1-2004 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 3.2 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1D
90.1-2007 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 3.2 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1D
90.1-2010 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 3.2 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1D before 10/08/2012
90.1-2013 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 3.7 | 0.052 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2013 Table 6.8.1-4
OEESC 2014 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 3.2 | 0.026 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(3)
NREL ZNE Ready 2017 | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 4.07 | 0.0572 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | PTHP | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  | 4.07 | 0.0572 | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | 10% better than 90.1-2016 Table 6.8.1-4
DOE Ref Pre-1980 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref Pre-1980 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref Pre-1980 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref Pre-1980 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.1 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.1 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
90.1-2004 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 6.6 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.1 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2007 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 7.7 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 7 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2007 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.1 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, Before 1/1/2010
90.1-2010 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 7.7 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2013 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 2014-12-31 | 7.7 |  |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-2, Before 1/1/2015
90.1-2013 | AirCooled | Single Package | 0 | 64999 | 2015-01-01 | 401655 | 8 |  |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-2, Before 1/1/2015
90.1-2013 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2013 Table 6.8.1-3
90.1-2013 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-5
90.1-2013 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-6
OEESC 2014 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | Single Package | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
NREL ZNE Ready 2017 | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From ZE AEDG Multifamily Committee
NREL ZNE Ready 2017 | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
NREL ZNE Ready 2017 | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
ZE AEDG Multifamily | AirCooled | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
ZE AEDG Multifamily | AirCooled | Single Package | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
DOE Ref Pre-1980 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref Pre-1980 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref Pre-1980 | SmallDuctHighVelocity | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
DOE Ref 1980-2004 | SmallDuctHighVelocity | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 since no DOE Reference Buildings had heat pumps
90.1-2004 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2004 | SmallDuctHighVelocity | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2004 Table 6.8.1B, Before 1/23/2006
90.1-2007 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 7.7 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2007 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 7.1 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2007 Table 6.8.1B, As of 1/23/2006
90.1-2010 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 7.7 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2010 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2010 Table 6.8.1B
90.1-2013 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 2014-12-31 | 7.7 |  |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-2, Before 1/1/2015
90.1-2013 | AirCooled | Split System | 0 | 64999 | 2015-01-01 | 401655 | 8.2 |  |  |  |  | HPACHeatCapFT | HPACHeatCapFFF | HPACHeatEIRFT | HPACHeatEIRFFF | HPACCOOLPLFFPLR | From 90.1-2013 Table 6.8.1-2, Before 1/1/2015
90.1-2013 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2013 Table 6.8.1-2
90.1-2013 | SmallDuctHighVelocity | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2013 Table 6.8.1-4
OEESC 2014 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 8.2 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | ThroughWall | Split System | 0 | 29999 | 1919-09-09 | 401655 | 7.4 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
OEESC 2014 | SmallDuctHighVelocity | Split System | 0 | 64999 | 1919-09-09 | 401655 | 6.8 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From OEESC2014 Table 503.2.3(2) Before 1/1/2016
NREL ZNE Ready 2017 | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 14 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From ZE AEDG Multifamily Committee
NREL ZNE Ready 2017 | AirCooled | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.3 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
NREL ZNE Ready 2017 | AirCooled | Split System | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
NREL ZNE Ready 2017 | AirCooled | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 14 |  |  |  |  | Minisplit-Heat-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Heat-EIR-fFF | Minisplit-Heat-PLF-fPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Minisplit System | 0 | 9999999 | 1919-09-09 | 401655 | 14 |  |  |  |  | Minisplit-Heat-Cap-fT | Minisplit-Cool-Cap-fFF | Minisplit-Heat-EIR-fT | Minisplit-Heat-EIR-fFF | Minisplit-Heat-PLF-fPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Split System | 0 | 64999 | 1919-09-09 | 401655 | 14 |  |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From ZE AEDG Multifamily Committee
ZE AEDG Multifamily | AirCooled | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 3.7 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2
ZE AEDG Multifamily | AirCooled | Split System | 135000 | 9999999 | 1919-09-09 | 401655 |  | 3.2 |  |  |  | DXHEAT-NECB2011-REF-CAPFT | DXHEAT-NECB2011-REF-CAPFFLOW | DXHEAT-NECB2011-REF-EIRFT | DXHEAT-NECB2011-REF-EIRFFLOW | DXHEAT-NECB2011-REF-PLFFPLR | From 90.1-2016 Table 6.8.1-2

## Unitary ACs
Each row represents the efficiency standards for a specificy type of unitary AC
Template | Cooling Type | Heating Type | Subcategory | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Minimum Seasonal Energy Efficiency Ratio (SEER) | Minimum Energy Efficiency Ratio (EER) | Minimum Integrated Part Load Value (kW/ton) | Minimum Integrated Energy Efficiency Ratio (IEER) | PTAC_EER_Coefficient_1 | PTAC_EER_Coefficient_2 | Minimum SCOP | COOL CAP FT | COOL CAP FFLOW | COOL EIR FT | COOL EIR FFLOW | COOL PLF FPLR | Notes
90.1-2004 | AirCooled | Electric Resistance or None | CRAC | 0 | 64999 | 1919-09-09 | 401655 | [6 empty] | 2.2 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2004 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2004 | AirCooled | Electric Resistance or None | CRAC | 65000 | 239999 | 1919-09-09 | 401655 | [6 empty] | 2.1 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2004 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2004 | AirCooled | Electric Resistance or None | CRAC | 240000 | 9999999 | 1919-09-09 | 401655 | [6 empty] | 1.9 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2004 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2007 | AirCooled | Electric Resistance or None | CRAC | 0 | 64999 | 1919-09-09 | 401655 | [6 empty] | 2.2 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2007 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2007 | AirCooled | Electric Resistance or None | CRAC | 65000 | 239999 | 1919-09-09 | 401655 | [6 empty] | 2.1 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2007 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2007 | AirCooled | Electric Resistance or None | CRAC | 240000 | 9999999 | 1919-09-09 | 401655 | [6 empty] | 1.9 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | 2007 not specified, follow ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2010 | AirCooled | Electric Resistance or None | CRAC | 0 | 64999 | 1919-09-09 | 401655 | [6 empty] | 2.2 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2010 Table 6.8.1K. capacity here is sensible only. SCOP for downflow units
90.1-2010 | AirCooled | Electric Resistance or None | CRAC | 65000 | 239999 | 1919-09-09 | 401655 | [6 empty] | 2.1 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2010 Table 6.8.1K. capacity here is sensible only. SCOP for downflow units
90.1-2010 | AirCooled | Electric Resistance or None | CRAC | 240000 | 9999999 | 1919-09-09 | 401655 | [6 empty] | 1.9 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2010 Table 6.8.1K. capacity here is sensible only. SCOP for downflow units
90.1-2013 | AirCooled | Electric Resistance or None | CRAC | 0 | 64999 | 1919-09-09 | 401655 | [6 empty] | 2.2 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2013 | AirCooled | Electric Resistance or None | CRAC | 65000 | 239999 | 1919-09-09 | 401655 | [6 empty] | 2.1 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
90.1-2013 | AirCooled | Electric Resistance or None | CRAC | 240000 | 9999999 | 1919-09-09 | 401655 | [6 empty] | 1.9 | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | ASHRAE 90.1-2013 Table 6.8.1-11. capacity here is sensible only. SCOP for downflow units
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref 1980-2004 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 10 | 0.16 |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
90.1-2004 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.5 | 0.213 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2004 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.5 | 0.213 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2007 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.5 | 0.213 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2007 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 12.5 | 0.213 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 13.8 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 13.8 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 2014-12-31 |  |  |  |  | 13.8 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 2014-12-31 |  |  |  |  | 13.8 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 2015-01-01 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2013 | AirCooled | All Other | PTAC | 0 | 9999999 | 2015-01-01 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
OEESC 2014 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
OEESC 2014 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | From 90.1-2016 Table 6.8.1-4
NREL ZNE Ready 2017 | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | From 90.1-2016 Table 6.8.1-4
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 11.06 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 11.06 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.28 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.28 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 8.92 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 8.92 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 8.9 | 8.3 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 8.9 | 8.3 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 135000 | 759999 | 1919-09-09 | 401655 |  | 8.5 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 759999 | 1919-09-09 | 401655 |  | 8.5 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.2 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.2 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 9.7 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.3 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.7 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.5 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.5 | 9.7 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.3 | 9.5 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.2 | 9.4 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.3 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.7 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.5 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.5 | 9.7 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.3 | 9.5 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.2 | 9.4 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11.2 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 | [5 empty] | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.8 | [5 empty] | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 10 |  | 9.7 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.8 |  | 9.7 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.7 |  | 9.4 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.2 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 2014-12-31 | 13 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 2015-01-01 | 401655 | 14 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 0 | 64999 | 2015-01-01 | 401655 | 14 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11.2 |  | 11.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.8 |  | 11 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 2015-12-31 |  | 10 |  | 10.1 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 2015-12-31 |  | 9.8 |  | 9.9 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.7 |  | 9.8 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.5 |  | 9.6 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 2016-01-01 | 401655 |  | 11.2 |  | 12.9 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 65000 | 134999 | 2016-01-01 | 401655 |  | 11 |  | 12.7 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 2016-01-01 | 401655 |  | 11 |  | 12.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.8 |  | 12.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 2016-01-01 | 401655 |  | 10 |  | 11.6 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 240000 | 759999 | 2016-01-01 | 401655 |  | 9.8 |  | 11.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 2016-01-01 | 401655 |  | 9.7 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Single Package | 760000 | 9999999 | 2016-01-01 | 401655 |  | 9.5 |  | 11 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXSEEREIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Single Package | 0 | 64999 | 1919-09-09 | 401655 | 14 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXSEEREIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.8 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Single Package | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 12.6 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Single Package | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 10 |  | 10.1 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Single Package | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.8 |  | 9.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.7 |  | 9.8 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Single Package | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
NREL ZNE Ready 2017 | AirCooled | All Other | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11.09 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 11.09 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 9.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.28 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.28 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 8.92 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 8.92 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref Pre-1980 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.63 | [5 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From DOE Pre-1980 Reference Buildings
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [6 empty] | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 8.9 | 8.3 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 8.9 | 8.3 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 135000 | 759999 | 1919-09-09 | 401655 |  | 8.5 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 759999 | 1919-09-09 | 401655 |  | 8.5 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.2 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
DOE Ref 1980-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 8.2 | 7.5 |  |  |  |  | DOE Ref DX Clg Coil Cool-Cap-fT | DOE Ref DX Clg Coil Cool-CAP-fFlow | DOE Ref DX Clg Coil Cool-EIR-fT | DOE Ref DX Clg Coil Cool-EIR-fFlow | DOE Ref DX Clg Coil Cool-PLF-fPLR | From 90.1-1989
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 10 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.3 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.7 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.5 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.5 | 9.7 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.3 | 9.5 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.2 | 9.4 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2004 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.3 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 10.1 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.7 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 9.5 | [5 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.5 | 9.7 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.3 | 9.5 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.2 | 9.4 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2007 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9 | 9.2 |  |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXSnglQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXSnglEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11.2 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 | [5 empty] | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 | [5 empty] | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.8 | [5 empty] | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 10 |  | 9.7 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.8 |  | 9.7 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.7 |  | 9.4 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2010 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.2 |  |  |  | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | AHU-1_CoolCStandard10Ton_CapFF | PSZ-AC_CoolCStandard10Ton_EIRFT | CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11.2 |  | 11.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 11 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 2015-12-31 |  | 10.8 |  | 11 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 2015-12-31 |  | 10 |  | 10.1 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 2015-12-31 |  | 9.8 |  | 9.9 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.7 |  | 9.8 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 2015-12-31 |  | 9.5 |  | 9.6 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 2016-01-01 | 401655 |  | 11.2 |  | 12.9 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 65000 | 134999 | 2016-01-01 | 401655 |  | 11 |  | 12.7 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 2016-01-01 | 401655 |  | 11 |  | 12.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 135000 | 239999 | 2016-01-01 | 401655 |  | 10.8 |  | 12.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 2016-01-01 | 401655 |  | 10 |  | 11.6 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 240000 | 759999 | 2016-01-01 | 401655 |  | 9.8 |  | 11.4 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 2016-01-01 | 401655 |  | 9.7 |  | 11.2 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
90.1-2013 | AirCooled | All Other | Split System | 760000 | 9999999 | 2016-01-01 | 401655 |  | 9.5 |  | 11 |  |  |  | PSZ-AC_Unitary_PackagecoolCapFT | PSZ-AC_Unitary_PackagecoolFFF | PSZ-AC DX Unitary Package EIRFT | PSZ-AC_Unitary_PackagecoolEIRFFF | PSZ-AC_Unitary_PackagecoolPLR
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXSEEREIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Split System | 0 | 64999 | 1919-09-09 | 401655 | 13 | [6 empty] | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXSEEREIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.8 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Split System | 65000 | 134999 | 1919-09-09 | 401655 |  | 11 |  | 12.6 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 11 |  | 11.2 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Split System | 135000 | 239999 | 1919-09-09 | 401655 |  | 10.8 |  | 11 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 10 |  | 10.1 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Split System | 240000 | 759999 | 1919-09-09 | 401655 |  | 9.8 |  | 9.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | Electric Resistance or None | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.7 |  | 9.8 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
OEESC 2014 | AirCooled | All Other | Split System | 760000 | 9999999 | 1919-09-09 | 401655 |  | 9.5 |  | 9.6 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac
NREL ZNE Ready 2017 | AirCooled | Electric Resistance or None | Split System | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
NREL ZNE Ready 2017 | AirCooled | All Other | Split System | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | All Other | PTAC | 0 | 9999999 | 1919-09-09 | 401655 |  |  |  |  | 14 | 0.3 |  | PSZ-Fine Storage DX Coil Cap-FT | DX Coil Cap-FF | PSZ-AC DX Coil EIR-FT | Split DX Coil EIR-FF | HPACCOOLPLFFPLR | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | All Other | Single Package | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | Electric Resistance or None | Split System | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4
ZE AEDG Multifamily | AirCooled | All Other | Split System | 0 | 9999999 | 1919-09-09 | 401655 |  | 11.2 |  | 12.9 |  |  |  | CoilClgDXQRatio_fTwbToadbSI | CoilClgDXDblQRatio_fCFMRatio | CoilClgDXEIRRatio_fTwbToadbSI | CoilClgDXDblEIRRatio_fCFMRatio | CoilClgDXEIRRatio_fQFrac | From 90.1-2016 Table 6.8.1-4

## Water Heaters
Each row represents the efficiency standards for a specific type of water heater
Template | Fuel Type | Minimum Capacity (Btu/hr) | Maximum Capacity (Btu/hr) | Start Date | End Date | Energy Factor Base (%) | Energy Factor Volume Derate (%/gal) | Standby Loss Base (Btu/hr) | Standby Loss Capacity Allowance (Btu/hr/Btu/hr) | Standby Loss Volume Allowance (Btu/hr/gal) | Hourly Loss Base (%) | Hourly Loss Volume Allowance (%/gal) | Thermal Efficiency (%) | Notes
DOE Ref Pre-1980 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.93 | 0.00132 | [6 empty] | From DOE Reference Buildings
DOE Ref 1980-2004 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.93 | 0.00132 | [6 empty] | From DOE Reference Buildings
90.1-2004 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.93 | 0.00132 | [6 empty] | From 90.1-2004 Table 7.8
90.1-2007 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.93 | 0.00132 | [6 empty] | From 90.1-2007 Table 7.8
90.1-2010 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.97 | 0.00132 | [6 empty] | From 90.1-2010 Table 7.8
90.1-2013 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.97 | 0.00132 | [6 empty] | From 90.1-2013 Table 7.8
NREL ZNE Ready 2017 | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.97 | 0.00132 | [6 empty] | Code of Federal Regulations 10 CFR Part 430.
DOE Ref Pre-1980 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From DOE Reference Buildings
DOE Ref 1980-2004 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From DOE Reference Buildings
90.1-2004 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2004 Table 7.8
90.1-2007 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2007 Table 7.8
90.1-2010 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2010 Table 7.8
90.1-2013 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2013 Table 7.8
NREL ZNE Ready 2017 | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2016 Table 7.8
DOE Ref Pre-1980 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | [7 empty] | 0.78 | From DOE Reference Buildings
DOE Ref 1980-2004 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | [7 empty] | 0.78 | From DOE Reference Buildings
90.1-2004 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.62 | 0.0019 | [6 empty] | From 90.1-2004 Table 7.8
90.1-2007 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.62 | 0.0019 | [6 empty] | From 90.1-2007 Table 7.8
90.1-2010 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.67 | 0.0019 | [6 empty] | From 90.1-2010 Table 7.8
90.1-2013 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.67 | 0.0019 | [6 empty] | From 90.1-2013 Table 7.8
NREL ZNE Ready 2017 | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.67 | 0.0019 | [6 empty] | Code of Federal Regulations 10 CFR Part 430.
DOE Ref Pre-1980 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 | [7 empty] | 0.78 | From DOE Reference Buildings
DOE Ref 1980-2004 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 | [7 empty] | 0.78 | From DOE Reference Buildings
90.1-2004 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 800 | 110 |  |  | 0.8 | From 90.1-2004 Table 7.8
90.1-2007 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 800 | 110 |  |  | 0.8 | From 90.1-2007 Table 7.8
90.1-2010 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 800 | 110 |  |  | 0.8 | From 90.1-2010 Table 7.8
90.1-2013 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 800 | 110 |  |  | 0.8 | From 90.1-2013 Table 7.8
NREL ZNE Ready 2017 | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 799 | 16.6 |  |  | 0.8 | From 90.1-2016 Table 7.8
ZE AEDG Multifamily | Electricity | 0 | 40945.99 | 1919-09-09 | 401655 | 0.97 | 0 | [6 empty] | Code of Federal Regulations 10 CFR Part 430.
ZE AEDG Multifamily | Electricity | 40946 | 99999999 | 1919-09-09 | 401655 |  |  | 20 |  | 35 |  |  |  | From 90.1-2016 Table 7.8
ZE AEDG Multifamily | NaturalGas | 0 | 74999.99 | 1919-09-09 | 401655 | 0.67 | 0 | [6 empty] | Code of Federal Regulations 10 CFR Part 430.
ZE AEDG Multifamily | NaturalGas | 75000 | 99999999 | 1919-09-09 | 401655 |  |  |  | 799 | 16.6 |  |  | 0.8 | From 90.1-2016 Table 7.8

## Elevators
Adding elevators to models
Template | Building Type | Elevator Type | Number of Elevators | Elevator Schedule | Elevator Fan Schedule | Area Per Passenger Elevator (ft2) | Units Per Passenger Elevator | Beds Per Passenger Elevator | Area Per Freight Elevator (ft2) | Units Per Freight Elevator | Beds Per Freight Elevator | Additional Passenger Elevators | Notes
90.1-2004 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2004 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2004 | HighriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2004 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
90.1-2004 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
90.1-2004 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2004 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2004 | LargeOfficeDetail |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2004 | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | MediumOfficeDetailed | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2004 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2004 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2004 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2004 | SecondarySchool | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
90.1-2004 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2004 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2004 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
90.1-2007 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2007 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2007 | HighriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2007 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
90.1-2007 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
90.1-2007 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2007 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2007 | LargeOfficeDetail |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2007 | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | MediumOfficeDetailed | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2007 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2007 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2007 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2007 | SecondarySchool | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
90.1-2007 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2007 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2007 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
90.1-2010 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2010 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2010 | HighriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2010 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
90.1-2010 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
90.1-2010 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2010 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2010 | LargeOfficeDetail |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2010 | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | MediumOfficeDetailed | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2010 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2010 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2010 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2010 | SecondarySchool | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
90.1-2010 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2010 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2010 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
90.1-2013 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2013 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2013 | HighriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2013 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
90.1-2013 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
90.1-2013 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2013 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2013 | LargeOfficeDetail |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
90.1-2013 | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | MediumOfficeDetailed | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
90.1-2013 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
90.1-2013 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2013 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2013 | SecondarySchool | Hydraulic | 2 | SchoolSecondary BLDG_ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_ADD_DF | 100000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
90.1-2013 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
90.1-2013 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
90.1-2013 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
DOE Ref 1980-2004 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref 1980-2004 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
DOE Ref 1980-2004 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
DOE Ref 1980-2004 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
90.1-2013 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
DOE Ref 1980-2004 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
DOE Ref 1980-2004 | MediumOffice | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | MediumOfficeDetailed | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
DOE Ref 1980-2004 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref 1980-2004 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref 1980-2004 | SecondarySchool | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | 100000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref 1980-2004 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref 1980-2004 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
DOE Ref Pre-1980 | Courthouse | Hydraulic | 5 | Courthouse BLDG ELEVATORS | Courthouse ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref Pre-1980 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
DOE Ref Pre-1980 | Hospital | Traction | 8 |  |  |  |  | 100 |  |  | 100 | 2 | DOE Prototype Buildings
DOE Ref Pre-1980 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  | 1 | DOE Prototype Buildings
DOE Ref 1980-2004 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | Office |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
DOE Ref Pre-1980 | LargeOffice |  |  |  |  | 45000 |  |  | 500000 |  |  |  | DOE Prototype Buildings
DOE Ref Pre-1980 | MediumOffice | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | MediumOfficeDetailed | Hydraulic | 2 | Medium Office BLDG ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | College | Hydraulic | 2 | College BLDG_ELEVATORS | College ELEV_LIGHT_FAN_SCH_24_7 | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | Outpatient | Hydraulic | 3 |  |  | 15000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | PrimarySchool |  | 0 |  |  | 100000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
DOE Ref Pre-1980 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref Pre-1980 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref Pre-1980 | SecondarySchool | Hydraulic | 2 | SecondarySchool BLDG ELEVATORS | SchoolSecondary ELEV_LIGHT_FAN_SCH_24_7 | 100000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | SmallHotel | Hydraulic | 2 |  |  |  | 75 | [5 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | SmallOffice |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | SmallOfficeDetailed |  | 0 |  |  | 45000 | [6 empty] | DOE Prototype Buildings
DOE Ref Pre-1980 | SuperMarket |  |  |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
DOE Ref Pre-1980 | Warehouse |  | 0 |  |  | 100000 |  |  | 250000 |  |  |  | DOE Prototype Buildings
NREL ZNE Ready 2017 | FullServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
NREL ZNE Ready 2017 | LargeHotel | Traction | 6 |  |  |  | 75 |  |  | 150 |  |  | DOE Prototype Buildings
NREL ZNE Ready 2017 | Office | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
NREL ZNE Ready 2017 | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
NREL ZNE Ready 2017 | MidriseApartment | Hydraulic | 1 | ApartmentMidRise BLDG_ELEVATORS | ApartmentMidRise ELEV_LIGHT_FAN_SCH_24_7 |  | 90 | [5 empty] | DOE Prototype Buildings
NREL ZNE Ready 2017 | QuickServiceRestaurant |  | 0 |  |  | 15000 | [6 empty] | Catchall set at 15000 ft^2 per elevator
NREL ZNE Ready 2017 | Retail |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
NREL ZNE Ready 2017 | StripMall |  | 0 |  |  | 45000 | [6 empty] | Assuming 45000 ft^2 per elevator as default for building types not in original code
ZE AEDG Multifamily | Office | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings
ZE AEDG Multifamily | MediumOffice | Hydraulic | 2 | OfficeMedium BLDG_ELEVATORS | OfficeMedium ELEV_LIGHT_FAN_SCH_ADD_DF | 45000 | [6 empty] | DOE Prototype Buildings

## Refrigeration System Lineup
Template | Building Type | Size Category | System Type | Number of display cases | Number of walkins | Case Type 1 | Case Type 2 | Case Type 3 | Case Type 4 | Case Type 5 | Case Type 6 | Case Type 7 | Case Type 8 | Case Type 9 | Case Type 10 | Case Type 11 | Case Type 12 | Case Type 13 | Case Type 14 | Walkin Type 1 | Walkin Type 2 | Walkin Type 3 | Walkin Type 4 | Walkin Type 5 | Walkin Type 6 | Walkin Type 7 | Walkin Type 8 | Compressor name
DOE Ref Pre-1980 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
DOE Ref Pre-1980 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
DOE Ref Pre-1980 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
DOE Ref Pre-1980 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
DOE Ref Pre-1980 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
DOE Ref 1980-2004 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
DOE Ref 1980-2004 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
DOE Ref 1980-2004 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
DOE Ref 1980-2004 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
DOE Ref 1980-2004 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2004 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
90.1-2004 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2004 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2004 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
90.1-2004 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2004 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2007 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
90.1-2007 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2007 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2007 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
90.1-2007 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2007 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2010 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
90.1-2010 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2010 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2010 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
90.1-2010 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2010 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2013 | SuperMarket | <35k ft2 | Medium Temperature | 7 | 4 | Deli Cases | Dairy Cases | Service Meat Cases | Beverage Cases | Produce Cases Med | Produce Cases Low | Service Bakery Cases | [7 empty] | Dairy Cooler | Meat Cooler | Deli Cooler | Produce Cooler |  |  |  |  | MT compressor_SmallandOld
90.1-2013 | SuperMarket | 35k - 50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2013 | SuperMarket | >50k ft2 | Medium Temperature | 14 | 8 | Deli Cases | Dairy Cases | Meat Cases Med | Meat Cases Low | Service Meat Cases | Beverage Cases | Service Deli Cases | Salad Cases | Produce Cases Med | Produce Cases Low | Produce Islands | Floral Cases | Service Bakery Cases | Prepared Foods Cases | Dairy Cooler | Beer Cooler | Meat Cooler | Meat Prep | Bloom Box | Deli Cooler | Produce Cooler | Fish Cooler | MT compressor
90.1-2013 | SuperMarket | <35k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor_SmallandOld
90.1-2013 | SuperMarket | 35k - 50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
90.1-2013 | SuperMarket | >50k ft2 | Low Temperature | 3 | 2 | Ice Cream Reach-Ins | Ice Cream Coffins | Frozen Food Reach-Ins | [11 empty] | Grocery Freezer | Bakery Freezer | [6 empty] | LT compressor
DOE Ref Pre-1980 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref Pre-1980 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor_SmallandOld
DOE Ref 1980-2004 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2004 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2007 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2010 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor_SmallandOld
90.1-2013 | PrimarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Primary School Freezer | [7 empty] | LT compressor
90.1-2013 | SecondarySchool | Any | Low Temperature | 0 | 1 | [14 empty] | Secondary School Freezer | [7 empty] | LT compressor
90.1-2013 | QuickServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Freezer | [7 empty] | LT compressor
90.1-2013 | FullServiceRestaurant | Any | Low Temperature | 0 | 1 | [14 empty] | Full Service Restaurant Freezer | [7 empty] | LT compressor
90.1-2013 | LargeHotel | Any | Low Temperature | 0 | 1 | [14 empty] | Large Hotel Freezer | [7 empty] | LT compressor
90.1-2013 | Hospital | Any | Low Temperature | 0 | 1 | [14 empty] | Hospital Freezer | [7 empty] | LT compressor
DOE Ref Pre-1980 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref Pre-1980 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref Pre-1980 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref Pre-1980 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref Pre-1980 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref Pre-1980 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor_SmallandOld
DOE Ref 1980-2004 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2004 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2007 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2010 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor_SmallandOld
90.1-2013 | PrimarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Primary School Cooler | [7 empty] | MT compressor
90.1-2013 | SecondarySchool | Any | Medium temperature | 0 | 1 | [14 empty] | Secondary School Cooler | [7 empty] | MT compressor
90.1-2013 | QuickServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Quick Service Restaurant Cooler | [7 empty] | MT compressor
90.1-2013 | FullServiceRestaurant | Any | Medium temperature | 0 | 1 | [14 empty] | Full Service Restaurant Cooler | [7 empty] | MT compressor
90.1-2013 | LargeHotel | Any | Medium temperature | 0 | 1 | [14 empty] | Large Hotel Cooler | [7 empty] | MT compressor
90.1-2013 | Hospital | Any | Medium temperature | 0 | 1 | [14 empty] | Hospital Cooler | [7 empty] | MT compressor

## Refrigeration System
Template | Building Type | Size Category | System Type | Refrigerant | SuctionTemperatureControlType
DOE Ref Pre-1980 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
DOE Ref Pre-1980 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
DOE Ref Pre-1980 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
DOE Ref Pre-1980 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
DOE Ref Pre-1980 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
90.1-2004 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
90.1-2004 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
90.1-2004 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
90.1-2004 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
90.1-2007 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
90.1-2007 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
90.1-2007 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
90.1-2007 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
90.1-2010 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
90.1-2010 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
90.1-2010 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
90.1-2010 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | SuperMarket | <35k ft2 | Medium Temperature | R22 | ConstantSuctionTemperature
90.1-2013 | SuperMarket | 35k - 50k ft2 | Medium Temperature | R507a | ConstantSuctionTemperature
90.1-2013 | SuperMarket | >50k ft2 | Medium Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | SuperMarket | <35k ft2 | Low Temperature | R22 | ConstantSuctionTemperature
90.1-2013 | SuperMarket | 35k - 50k ft2 | Low Temperature | R507a | ConstantSuctionTemperature
90.1-2013 | SuperMarket | >50k ft2 | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2004 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2007 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2010 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | PrimarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | SecondarySchool | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | College | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | QuickServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | FullServiceRestaurant | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | LargeHotel | Any | Low Temperature | R404a | ConstantSuctionTemperature
90.1-2013 | Hospital | Any | Low Temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref Pre-1980 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
DOE Ref 1980-2004 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2004 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2007 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2010 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | PrimarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | SecondarySchool | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | QuickServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | FullServiceRestaurant | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | LargeHotel | Any | Medium temperature | R404a | ConstantSuctionTemperature
90.1-2013 | Hospital | Any | Medium temperature | R404a | ConstantSuctionTemperature

## Refrigerated Cases
Template | Size Category | Case Type | Case Category | Case Model | ft_tube_per_ft_case | Latent Heat Ratio | Rated runtime Fraction | Case Length | Case Temp | Cooling Capacity per Length | Evap Fan Power per Length | Evap Temp | Lighting per ft | Fraction of Lighting Energy to Case | Latent Case Credit Curve Name | Defrost Power per Length | Defrost Type | Defrost Correction Type | Defrost Correction Curve Name | Anti-Sweat Power | Minimum Anti-Sweat Heater Power per Unit Length | Anti-Sweat Heater Control | FractionofAntiSweatHeaterEnergytoCase | Under Case HVAC Return Air Fraction | Restocking Schedule | Lighting Schedule | Minutes Defrost | Defrost per day | Minutes Dripdown | Dripdown per day | Notes
DOE Ref Pre-1980 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -14.98 | 695.2 | 7.1933 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 435.9859 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 77.6021 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 617.4 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref Pre-1980 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref Pre-1980 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref Pre-1980 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref Pre-1980 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref Pre-1980 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -14.98 | 695.2 | 7.1933 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 435.9859 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 77.6021 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 617.4 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
DOE Ref 1980-2004 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref 1980-2004 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref 1980-2004 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
DOE Ref 1980-2004 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
DOE Ref 1980-2004 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -14.98 | 695.2 | 7.1933 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 435.9859 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 77.6021 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 617.4 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2004 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2004 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2004 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2004 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -14.98 | 695.2 | 7.1933 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 435.9859 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 77.6021 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 617.4 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2007 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2007 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2007 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2007 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2007 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -14.98 | 695.2 | 7.1933 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 435.9859 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 77.6021 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 583.7 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 617.4 | 21.4 | -17.32 | 30.1996 | 0.5 | Glass Door Latent Curve Case | 372.3132 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 87.3862 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 410 | 15.4991 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2010 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2010 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2010 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2010 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 808 | 9.6987 | 20.48 | 21.7993 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2010 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1437.6 | 13.1003 | 24.98 | 22.101 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Ice Cream Coffins |  | othercase | 3.775 | 0.2 | 0.85 | 7.874 | -18.94 | 521.2 | 1.6703 | -22 | 0 | 0.5 | Coffin Latent Curve Case | 256.0015 | ElectricwithTemperatureTermination | DewpointMethod | Coffin Defrost Curve | 23.9878 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Frozen Food Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 135.8268 | -4 | 426 | 9.0007 | -10.3 | 7.8395 | 0.5 | Glass Door Latent Curve Case | 295.9913 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 42.4891 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Deli Cases |  | reachin | 3.775 | 0.1 | 0.85 | 83.6614 | -4 | 426 | 9.0007 | -10.3 | 7.8395 | 0.5 | Glass Door Latent Curve Case | 295.9913 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 42.4891 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Ice Cream Reach-Ins |  | reachin | 3.775 | 0.1 | 0.85 | 143.7008 | -11.02 | 452 | 9.0007 | -17.32 | 7.8395 | 0.5 | Glass Door Latent Curve Case | 295.9913 | ElectricwithTemperatureTermination | DewpointMethod | Glass Door Defrost Curve | 42.4891 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Produce Cases Med |  | othercase | 2.7625 | 0.2 | 0.85 | 23.95 | 26.78 | 302.9 | 2.03 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Produce Islands |  | othercase | 2.7625 | 0.2 | 0.85 | 36.09 | 26.78 | 302.9 | 2.03 | 20.48 | 0 | 0.5 | Coffin Latent Curve Case | 261.0002 | ElectricwithTemperatureTermination | None | Coffin Defrost Curve | 19.3853 |  |  | 0.7 |  | Always Off | Always On | 45 | 1 | 55 | 1
90.1-2013 | Any | Dairy Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 23.95 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Dairy_Meat Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 60.04 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Meat Cases Med |  | othercase | 2.7625 | 0.3 | 0.85 | 20.01 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Beverage Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 16.08 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Service Meat Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 20.01 | 26.78 | 599.1 | 6.221 | 20.48 | 5.4011 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.2938 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2013 | Any | Service Deli Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 43.96 | 26.78 | 599.1 | 6.221 | 20.48 | 5.4011 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.2938 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2013 | Any | Salad Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 47.9 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Floral Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 12.14 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2013 | Any | Service Bakery Cases |  | servicecase | 2.7625 | 0.1 | 0.85 | 7.87 | 26.78 | 599.1 | 6.221 | 20.48 | 5.4011 | 0.5 | Glass Door Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 19.2938 |  |  | 0.7 |  | Always Off | Always On | 40 | 4 | 50 | 4
90.1-2013 | Any | Prepared Foods Cases |  | othercase | 2.7625 | 0.3 | 0.85 | 55.77 | 33.08 | 1143.4 | 4.9195 | 24.98 | 4.9804 | 0.5 | Open Latent Curve Case | 0 | OffCycle | None | Coffin Defrost Curve | 0 |  |  | 0.7 |  | Always Off | Always On | 30 | 4 | 40 | 4
90.1-2004 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 20.4216 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2004 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 20.4216 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2007 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary BLDG_LIGHT_SCH_2010 |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 20.4216 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2010 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary BLDG_LIGHT_SCH_2010 |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 5.7477 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 4.7897 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 5.7477 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 4.7897 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 4.7897 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 5.8347 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
90.1-2013 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 4.7897 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary walkin_occ_lght_SCH |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 20.4216 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref 1980-2004 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Full Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantSitDown Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Large Hotel | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | HotelLarge BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Quick Service Restaurant | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 10.0066 | 35.6 | 763.3752 | 20.1168 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Secondary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolSecondary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case College | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 24.0157 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | College BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Hospital | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 29.2979 | 35.6 | 921.9784 | 20.4216 |  | 12.192 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | Hospital BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L
DOE Ref Pre-1980 | Any | Case Primary School | Deli Cases | Hussman_D5L | 2.7625 | 0.08 | 0.85 | 12.0079 | 35.6 | 763.3752 | 16.764 |  | 10.0584 | 1 | Refrigeration Case Latent Credit Curve | 0 | None | None |  |  |  | None | 0.2 | 0.05 | SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASE_CaseStockingSched | SchoolPrimary BLDG_LIGHT_SCH |  |  |  |  | Hussman_D5L

## Refrigeration Walkins
Template | Size Category | Walkin Type | Rated Cooling Capacity | Cooling Capacity c2 | Cooling Capacity c1 | Cooling Capacity c0 | Operating Temp | Source Temp | Defrost Control Type | Defrost Type | Defrost Power Mult | Defrost Power | RatedTotalHeatingPower | RatedCirculationFanPower | Motor Category | Fan Power | Fan Power Mult | Lighting Power | Lighting Power Mult | Insulated Floor U | Insulated Surface U | Stocking Door U | Reachin Door Area Mult | Glass reachin door U value | Reachin Door Area | Total Insulated Surface Area | Height of glass reachin doors | Area of stocking doors | Floor Surface Area | Height of stocking doors | TemperatureTerminationDefrostFractiontoIce | Restocking Schedule | Lighting Schedule | Minutes Defrost | Defrost per day | Minutes Dripdown | Dripdown per day | Doorway protection type
90.1-2004 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | [5 empty] | 516.6528 |  |  | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | QuickServiceRestaurant Bldg Light | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2004 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
90.1-2004 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2004 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2004 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2004 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2004 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2004 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
90.1-2007 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2007 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2007 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2007 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2007 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2007 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2007 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantSitDown BLDG_LIGHT_KITCHEN_SCH_2004_2007 | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantFastFood walkin_occ_lght_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2010 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2010 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.052 |  | 5.4 | 0.203 | 0.177 | 0.177 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.052 |  | 5.4 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 51.5886 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | FullServiceRestaurant Bldg Light | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 51.5889 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 188.5 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 188.5 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | StripCurtain
90.1-2013 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 51.5889 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 51.5886 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
90.1-2013 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | StripCurtain
DOE Ref 1980-2004 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantSitDown walkin_occ_lght_SCH | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantFastFood BLDG_LIGHT_DINING_SCH_2004_2007 | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
DOE Ref 1980-2004 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref 1980-2004 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref 1980-2004 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref 1980-2004 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref 1980-2004 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref 1980-2004 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref 1980-2004 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Freezer |  | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Cooler |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Cooler Glass Door |  | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 |  | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | [8 empty] | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Grocery Freezer | 28674.8709 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 516.6672 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Bakery Freezer | 9881.3706 | -0.3087 | 152.9 | 1060 | -14.98 | -25.06 | TemperatureTermination | Electric | 0.79 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 0.203 | 0.177 | 0.177 | 0 | 0.39973 |  |  | 6 | 35.5221 | 129.1668 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Dairy Cooler | 41526.8344 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 667.3618 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Beer Cooler | 30403.03 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0.35 | 0.39973 |  |  | 6 | 35.5221 | 473.6116 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Meat Cooler | 26695.0952 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 409.0282 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Meat Prep | 37818.8996 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 602.7784 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Bloom Box | 6919.4429 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 64.5834 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Deli Cooler | 10009.3885 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 118.4029 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Produce Cooler | 26077.106 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 398.2643 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Fish Cooler | 7537.432 | -0.3387 | 181 | 941.2 | 35.006 | 24.998 | TimeSchedule | OffCycle | 0 |  | 0 | 0 | SPM |  | 0.08 |  | 10.8 | 2.27 | 0.203 | 0.203 | 0 | 0.39973 |  |  | 6 | 35.5221 | 75.3473 | 6.8898 | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Full Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 2000.8 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantSitDown Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | RestaurantSitDown walkin_occ_lght_SCH | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Primary School | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1500.6 | 0 | 0 | SPM | 249.978 |  | 120.78 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Large Hotel | 9166.5148 |  |  |  | -9.4 | -19 |  | Electric |  | 1998.36 | 0 | 0 | SPM | 248.88 |  | 120.048 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZER_WalkInStockingSched | HotelLarge BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Quick Service Restaurant | 5728.031 |  |  |  | -9.4 | -19 |  | Electric |  | 3151.748 | 0 | 0 | SPM | 180.56 |  | 80.52 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | RestaurantFastFood Kitchen_Case:1_WALKINFREEZER_WalkInStockingSched | QuickServiceRestaurant Bldg Light | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In Secondary School | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Walk-In College | 18333.0295 |  |  |  | -9.4 | -19 |  | Electric |  | 3001.2 | 0 | 0 | SPM | 500 |  | 241.56 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | SchoolSecondary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZER_WalkInStockingSched | SchoolSecondary BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | StripCurtain
DOE Ref Pre-1980 | Any | Walk-In Hospital | 27499.5443 |  |  |  | -9.4 | -19 |  | Electric |  | 3996.72 | 0 | 0 | SPM | 757.62 |  | 362.34 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Hospital Kitchen_Flr_5_Case:1_WALKINFREEZER_WalkInStockingSched | Hospital BLDG_LIGHT_SCH | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Primary School Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Secondary School Cooler | 19100 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 400 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Quick Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Full Service Restaurant Cooler | 7700 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 100 |  |  |  |  | 0 | [5 empty] | 100 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Large Hotel Cooler | 9200 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 200 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Hospital Cooler | 27000 |  |  |  | 35.6 | 25 |  | OffCycle |  | 0 |  |  | SPM | 600 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 60 | 2 | 60 | 2 | None
DOE Ref Pre-1980 | Any | Primary School Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Secondary School Freezer | 18300 |  |  |  | -9.4 | -19 |  | Electric |  | 3000 |  |  | SPM | 500 |  | 240 |  |  |  |  | 0 | [5 empty] | 240 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Quick Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Full Service Restaurant Freezer | 5700 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 180 |  | 80 |  |  |  |  | 0 | [5 empty] | 80 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Large Hotel Freezer | 9200 |  |  |  | -9.4 | -19 |  | Electric |  | 2000 |  |  | SPM | 250 |  | 120 |  |  |  |  | 0 | [5 empty] | 120 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None
DOE Ref Pre-1980 | Any | Hospital Freezer | 27500 |  |  |  | -9.4 | -19 |  | Electric |  | 4000 |  |  | SPM | 760 |  | 360 |  |  |  |  | 0 | [5 empty] | 360 |  | 0.7 | Always Off | Always On | 45 | 2 | 45 | 2 | None

## Refrigeration Condenser
Template | Building Type | System Type | Size Category | Subcool T | HeatRejectionCurve_C1 | Min Airflow | Fan Power per Q Rejected | Fan Speed Control | RatedEffectiveTotalHeatRejectionRateCurve | Notes
DOE Ref Pre-1980 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.026 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.0218 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.026 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.0218 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref 1980-2004 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.026 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.0218 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2004 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.026 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.0218 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2010 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2013 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
DOE Ref Pre-1980 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref Pre-1980 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
DOE Ref Pre-1980 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref Pre-1980 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref Pre-1980 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref Pre-1980 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
DOE Ref 1980-2004 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref 1980-2004 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
DOE Ref 1980-2004 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref 1980-2004 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref 1980-2004 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref 1980-2004 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2004 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2004 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2004 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2004 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2004 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2004 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2007 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2007 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2007 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2007 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2007 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2007 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2010 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2010 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2010 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2010 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2010 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2010 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2013 | PrimarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2013 | SecondarySchool | Low Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2013 | QuickServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2013 | FullServiceRestaurant | Low Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2013 | LargeHotel | Low Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2013 | Hospital | Low Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
DOE Ref Pre-1980 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref Pre-1980 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
DOE Ref Pre-1980 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref Pre-1980 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref Pre-1980 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref Pre-1980 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
DOE Ref 1980-2004 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref 1980-2004 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
DOE Ref 1980-2004 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref 1980-2004 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
DOE Ref 1980-2004 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
DOE Ref 1980-2004 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2004 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2004 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2004 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2004 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2004 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2004 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2007 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2007 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2007 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2007 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2007 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2007 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2010 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2010 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2010 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2010 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2010 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2010 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2013 | PrimarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2013 | SecondarySchool | Medium Temperature | Any | 2 | 22000 | 0 | 0.039267 | VariableSpeed
90.1-2013 | QuickServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2013 | FullServiceRestaurant | Medium Temperature | Any | 2 | 22000 | 0 | 0.042857 | VariableSpeed
90.1-2013 | LargeHotel | Medium Temperature | Any | 2 | 22000 | 0 | 0.038043 | VariableSpeed
90.1-2013 | Hospital | Medium Temperature | Any | 2 | 22000 | 0 | 0.037037 | VariableSpeed
90.1-2007 | SuperMarket | Medium Temperature | <35k ft2 | 2 | 597289 | 0 | 0.026 | FixedLinear | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2007 | SuperMarket | Medium Temperature | 35k - 50k ft2 | 2 | 597289 | 0 | 0.026 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2007 | SuperMarket | Medium Temperature | >50k ft2 | 2 | 597289 | 0 | 0.0234 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2007 | SuperMarket | Low Temperature | <35k ft2 | 2 | 254451.35 | 0 | 0.0218 | FixedLinear | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2007 | SuperMarket | Low Temperature | 35k - 50k ft2 | 2 | 254451.35 | 0 | 0.0218 | VariableSpeed | DEER_Heat_Rejections_MT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan
90.1-2007 | SuperMarket | Low Temperature | >50k ft2 | 2 | 254451.35 | 0 | 0.01962 | VariableSpeed | DEER_Heat_Rejections_LT | HeatRejectionCurve_C1 is in W/C, FanPowerperQRejected is in W/(BTU/h). Large Buildings and new vintages have 10% more efficient fan

## Refrigeration Compressors
Each row sets the properties for refrigeration compressors (like those used in grocery stores)
Template | Compressor Name | Compressor Type | Power Curve | Capacity Curve | Rated capacity | Notes
DOE Ref Pre-1980 | Low Temp | Low Temp | Old_Low_Temp_Comp_Pwr_Curve | Old_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
DOE Ref Pre-1980 | Med Temp | Med Temp | Old_Med_Temp_Comp_Pwr_Curve | Old_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
DOE Ref 1980-2004 | Low Temp | Low Temp | Old_Low_Temp_Comp_Pwr_Curve | Old_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
DOE Ref 1980-2004 | Med Temp | Med Temp | Old_Med_Temp_Comp_Pwr_Curve | Old_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
90.1-2004 | Low Temp | Low Temp | Old_Low_Temp_Comp_Pwr_Curve | Old_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
90.1-2004 | Med Temp | Med Temp | Old_Med_Temp_Comp_Pwr_Curve | Old_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
90.1-2007 | Low Temp | Low Temp | Old_Low_Temp_Comp_Pwr_Curve | Old_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
90.1-2007 | Med Temp | Med Temp | Old_Med_Temp_Comp_Pwr_Curve | Old_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
90.1-2010 | Low Temp | Low Temp | Old_Low_Temp_Comp_Pwr_Curve | Old_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
90.1-2010 | Med Temp | Med Temp | Old_Med_Temp_Comp_Pwr_Curve | Old_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
90.1-2013 | Low Temp | Low Temp | New_Low_Temp_Comp_Pwr_Curve | New_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
90.1-2013 | Med Temp | Med Temp | New_Med_Temp_Comp_Pwr_Curve | New_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
NREL ZNE Ready 2017 | Low Temp | Low Temp | New_Low_Temp_Comp_Pwr_Curve | New_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
NREL ZNE Ready 2017 | Med Temp | Med Temp | New_Med_Temp_Comp_Pwr_Curve | New_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
ZE AEDG Multifamily | Low Temp | Low Temp | New_Low_Temp_Comp_Pwr_Curve | New_Low_Temp_Comp_Cap_Curve | 83897.7475 | rated capacity in BTU/h
ZE AEDG Multifamily | Med Temp | Med Temp | New_Med_Temp_Comp_Pwr_Curve | New_Med_Temp_Comp_Cap_Curve | 203827.7145 | rated capacity in BTU/h
DOE Ref Pre-1980 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
DOE Ref Pre-1980 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
DOE Ref Pre-1980 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
DOE Ref Pre-1980 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h
DOE Ref 1980-2004 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
DOE Ref 1980-2004 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
DOE Ref 1980-2004 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
DOE Ref 1980-2004 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h
90.1-2004 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
90.1-2004 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
90.1-2004 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
90.1-2004 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h
90.1-2007 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
90.1-2007 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
90.1-2007 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
90.1-2007 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h
90.1-2010 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
90.1-2010 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
90.1-2010 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
90.1-2010 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h
90.1-2013 | MT compressor | Medium Temperature | MT_compressor_power | MT_compressor_capacity | 143415.725 | rated capacity in BTU/h
90.1-2013 | LT compressor | Low Temperature | LT_compressor_power | LT_compressor_capacity | 50567.94 | rated capacity in BTU/h
90.1-2013 | MT compressor_SmallandOld | Medium Temperature | MT_compressor_power_smallandold | MT_compressor_capacity_smallandold | 17599.82 | rated capacity in BTU/h
90.1-2013 | LT compressor_SmallandOld | Low Temperature | LT_compressor_power_smallandold | LT_compressor_capacity_smallandold | 36499.679 | rated capacity in BTU/h

## Economizers
Each row sets the economizer capacity limits for a particular template and climate zone
(blank = no economizer required)
Template | Climate Zone | Data Center | Capacity Limit (Btu/hr) | Notes
90.1-2004 | ASHRAE 169-2006-1A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-1A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-1B | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-1B | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-2A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-2A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-2B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-2B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-3C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-4C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-5C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-6A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-6A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-6B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-6B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-7A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-7A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-7B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-7B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-8A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-8A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-8B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2006-8B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-1A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-1A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-1B | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-1B | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-2A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-2A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-2B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-2B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-3C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4A | FALSE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4A | TRUE |  | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-4C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5C | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-5C | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-6A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-6A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-6B | FALSE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-6B | TRUE | 65000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-7A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-7A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-7B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-7B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-8A | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-8A | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-8B | FALSE | 135000 | 90.1-2004 Table 6.5.1
90.1-2004 | ASHRAE 169-2013-8B | TRUE | 135000 | 90.1-2004 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-1A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-1A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-1B | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-1B | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-2A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-2A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-2B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-2B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-3C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-4C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-5C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-6A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-6A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-6B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-6B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-7A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-7A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-7B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-7B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-8A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-8A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-8B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2006-8B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-1A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-1A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-1B | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-1B | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-2A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-2A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-2B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-2B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-3C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4A | FALSE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4A | TRUE |  | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-4C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5C | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-5C | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-6A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-6A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-6B | FALSE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-6B | TRUE | 65000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-7A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-7A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-7B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-7B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-8A | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-8A | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-8B | FALSE | 135000 | 90.1-2007 Table 6.5.1
90.1-2007 | ASHRAE 169-2013-8B | TRUE | 135000 | 90.1-2007 Table 6.5.1
90.1-2010 | ASHRAE 169-2006-1A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-1A | FALSE |  | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-1B | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-1B | FALSE |  | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-2A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-2A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-2B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-2B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-3A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-3A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-3B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-3B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-3C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-3C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-4A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-4A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-4B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-4B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-4C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-4C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-5A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-5A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-5B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-5B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-5C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-5C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-6A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-6A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-6B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-6B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-7A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-7A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-7B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-7B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-8A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-8A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2006-8B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2006-8B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-1A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-1A | FALSE |  | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-1B | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-1B | FALSE |  | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-2A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-2A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-2B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-2B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-3A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-3A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-3B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-3B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-3C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-3C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-4A | TRUE |  | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-4A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-4B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-4B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-4C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-4C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-5A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-5A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-5B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-5B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-5C | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-5C | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-6A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-6A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-6B | TRUE | 65000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-6B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-7A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-7A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-7B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-7B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-8A | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-8A | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2010 | ASHRAE 169-2013-8B | TRUE | 135000 | 90.1-2010 Table 6.5.1B
90.1-2010 | ASHRAE 169-2013-8B | FALSE | 54000 | 90.1-2010 Table 6.5.1A
90.1-2013 | ASHRAE 169-2006-1A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-1A | FALSE |  | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-1B | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-1B | FALSE |  | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-2A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-2A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-2B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-2B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-3A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-3A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-3B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-3B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-3C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-3C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-4A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-4A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-4B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-4B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-4C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-4C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-5A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-5A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-5B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-5B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-5C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-5C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-6A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-6A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-6B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-6B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-7A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-7A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-7B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-7B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-8A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-8A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2006-8B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2006-8B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-1A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-1A | FALSE |  | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-1B | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-1B | FALSE |  | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-2A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-2A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-2B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-2B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-3A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-3A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-3B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-3B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-3C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-3C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-4A | TRUE |  | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-4A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-4B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-4B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-4C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-4C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-5A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-5A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-5B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-5B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-5C | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-5C | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-6A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-6A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-6B | TRUE | 65000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-6B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-7A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-7A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-7B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-7B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-8A | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-8A | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
90.1-2013 | ASHRAE 169-2013-8B | TRUE | 135000 | 90.1-2013 Table 6.5.1-2
90.1-2013 | ASHRAE 169-2013-8B | FALSE | 54000 | 90.1-2013 Table 6.5.1-1
DOE Ref 1980-2004 | ASHRAE 169-2006-1A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-1B | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-2A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-2B | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-3A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-3B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-3C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-4A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-4B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-4C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-5A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-5B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-5C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-6A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-6B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-7A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-7B | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-8A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2006-8B | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-1A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-1B | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-2A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-2B | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-3A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-3B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-3C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-4A | FALSE |  | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-4B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-4C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-5A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-5B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-5C | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-6A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-6B | FALSE | 65000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-7A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-7B | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-8A | FALSE | 35000 | Same as 90.1-2004
DOE Ref 1980-2004 | ASHRAE 169-2013-8B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-1A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-1B | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-2A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-2B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-3A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-3B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-3C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-4A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-4B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-4C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-5A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-5B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-5C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-6A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-6B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-7A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-7B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-8A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2006-8B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-1A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-1B | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-2A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-2B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-3A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-3B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-3C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-4A | FALSE |  | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-4B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-4C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-5A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-5B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-5C | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-6A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-6B | FALSE | 65000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-7A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-7B | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-8A | FALSE | 35000 | Same as 90.1-2004
DOE Ref Pre-1980 | ASHRAE 169-2013-8B | FALSE | 35000 | Same as 90.1-2004
NREL ZNE Ready 2017 | ASHRAE 169-2006-1A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-1A | FALSE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-1B | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-1B | FALSE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-2A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-2A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-2B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-2B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-3C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-4C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-5C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-6A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-6A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-6B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-6B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-7A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-7A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-7B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-7B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-8A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-8A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-8B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2006-8B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-1A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-1A | FALSE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-1B | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-1B | FALSE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-2A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-2A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-2B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-2B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-3C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4A | TRUE |  | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-4C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5C | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-5C | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-6A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-6A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-6B | TRUE | 65000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-6B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-7A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-7A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-7B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-7B | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-8A | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-8A | FALSE | 54000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-8B | TRUE | 135000 | Same as 90.1-2013
NREL ZNE Ready 2017 | ASHRAE 169-2013-8B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-1A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-1A | FALSE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-1B | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-1B | FALSE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-2A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-2A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-2B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-2B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-3C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-4C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-5C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-6A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-6A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-6B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-6B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-7A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-7A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-7B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-7B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-8A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-8A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-8B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2006-8B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-1A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-1A | FALSE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-1B | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-1B | FALSE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-2A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-2A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-2B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-2B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-3C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4A | TRUE |  | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-4C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5C | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-5C | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-6A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-6A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-6B | TRUE | 65000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-6B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-7A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-7A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-7B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-7B | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-8A | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-8A | FALSE | 54000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-8B | TRUE | 135000 | Same as 90.1-2013
ZE AEDG Multifamily | ASHRAE 169-2013-8B | FALSE | 54000 | Same as 90.1-2013

## Curves
Performance Curves - This will be the only curve tab, the other Curve tabs will be deleted
Name | Category | Form | Dependent Variable | Independent Variable 1 | Independent Variable 2 | coeff_1 | coeff_2 | coeff_3 | coeff_4 | coeff_5 | coeff_6 | coeff_7 | coeff_8 | coeff_9 | coeff_10 | Minimum Independent Variable 1 | Maximum Independent Variable 1 | Minimum Independent Variable 2 | Maximum Independent Variable 2 | Minimum Dependent Variable Output | Maximum Dependent Variable Output | notes
a-Si_Spectral-fAirMass | PV-Module | Cubic |  | AirMass |  | coeff_1: 0.99264; coeff_2: 0.053349; coeff_3: -0.037202; coeff_4: 0.0032703 | [6 empty] | From .dat files included with MASControl2
Absor-1-Cap-fCHWT&ECT | 1-StageAbsorptn | BiQuadratic | QRatio | CHWT | ECT | 1.7574 | 0.054774 | -0.0029063 | -0.035145 | -0.000156 | 0.000894 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Absor-1-HIR-fCHWT&ECT | 1-StageAbsorptn | BiQuadratic |  | CHWT | ECT | 0.69115 | 0 | 0 | 0.005355 | 0.000178 | 0 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Absor-1-HIR-fPLR | 1-StageAbsorptn | Quadratic |  | PLR |  | coeff_1: 0.087773; coeff_2: 0.74492; coeff_3: 0.16731 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Absor-2-Cap-fCHWT&ECT | 2-StageAbsorptn | BiQuadratic | QRatio | CHWT | ECT | 0.36207 | 0.0001386 | 0.001458 | 0.073388 | -0.0020606 | 0.00101 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Absor-2-HIR-fCHWT&ECT | 2-StageAbsorptn | BiQuadratic |  | CHWT | ECT | 0.98675 | 0 | 0 | -0.0234 | 0.00081 | 0 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Absor-2-HIR-fPLR | 2-StageAbsorptn | Quadratic |  | PLR |  | coeff_1: 0.13551; coeff_2: 0.61798; coeff_3: 0.24651 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
AHU-1_CoolCStandard10Ton_CapFF | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.77136; coeff_2: 0.34053; coeff_3: -0.11088 | 0.75918 | 1.1388 |  |  |  |  | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
AirCooled_Chiller_2004_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 1.0434 | 0.040708 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 |  |  |  |  | 5 | 10 | 12.7 | 51.67 |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2004_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 |  |  |  |  | 5 | 10 | 12.7 | 51.67 |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 1.0434 | 0.040707 | 0.0004506 | -0.0041514 | -8.86e-05 | -0.0003467 |  |  |  |  | 5 | 10 | 12.7 | 51.67 |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_2010_PathA_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.59619 | -0.0099496 | 0.0007888 | 0.0004506 | 0.0004875 | -0.0007623 |  |  |  |  | 5 | 10 | 12.7 | 51.67 |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_AllCapacities_2004_2010_EIRFPLR | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.141; coeff_2: 0.655; coeff_3: 0.203 | 0 | 1 |  |  |  |  | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all AirCooled Chillers
AirCooled_Chiller_GT150_2004_EIRFPLR | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.141; coeff_2: 0.655; coeff_3: 0.203 | 0 | 1 |  |  |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_GT150_2010_PathA_EIRFPLR | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.141; coeff_2: 0.655; coeff_3: 0.203 | 0 | 1 |  |  |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_LT150_2004_EIRFPLR | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.141; coeff_2: 0.655; coeff_3: 0.203 | 0 | 1 |  |  |  |  | Based on Dick Lord's study dated January 17, 2010.
AirCooled_Chiller_LT150_2010_PathA_EIRFPLR | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.141; coeff_2: 0.655; coeff_3: 0.203 | 0 | 1 |  |  |  |  | Based on Dick Lord's study dated January 17, 2010.
AirFoil w Dischrg Dampers FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.22714; coeff_2: 1.1789; coeff_3: -0.41071 |  |  |  |  | 0.68 | 1 | From .dat files included with MASControl2
AirFoil w Inlet Vanes FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.58435; coeff_2: -0.57917; coeff_3: 0.97024 |  |  |  |  | 0.48 | 1 | From .dat files included with MASControl2
Atmospheric-Blr-HIR-fPLR | FuelBoilers | Quadratic |  | PLR |  | coeff_1: 0.027; coeff_2: 1.1055; coeff_3: -0.1325 | [6 empty] | From .dat files included with MASControl2
Boiler Constant Efficiency Curve | Boiler | Cubic | FIRRatio | QRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0; coeff_4: 0 | 0 | 1 |  |  |  |  | From DOE Reference Building
Boiler with Minimum Turndown | Boiler | Cubic | FIRRatio | QRatio |  | coeff_1: 0.7791; coeff_2: 1.4745; coeff_3: -2.5795; coeff_4: 1.3467 | 0 | 1.3 |  |  |  |  | From Regression of Prototype Building EMS
Boiler with No Minimum Turndown | Boiler | Cubic | FIRRatio | QRatio |  | coeff_1: 0.7463; coeff_2: 1.3196; coeff_3: -2.2154; coeff_4: 1.1674 | 0 | 1.3 |  |  |  |  | From Regression of Prototype Building EMS
BOILER-EFFFPLR-NECB2011 | Boiler | Cubic | FIRRatio | QRatio |  | coeff_1: 0.2901; coeff_2: 2.6664; coeff_3: -3.764; coeff_4: 1.82 | 0 | 1 |  |  |  |  | From NECB 2011
CdTe_Spectral-fAirMass | PV-Module | Cubic |  | AirMass |  | coeff_1: 0.93701; coeff_2: 0.051307; coeff_3: -0.0064664; coeff_4: 0.00017267 | [6 empty] | From .dat files included with MASControl2
CentChlrAirCoolCap-fCHW&OAT | Chiller | BiQuadratic | QRatio | CHWT | OAT | 0.94533 | 0.068474 | -0.0033617 | 0.00010811 | -0.000225 | 8.2e-05 | [10 empty] | From .dat files included with MASControl2
CentChlrAirCoolEIR-fCHW&OAT | Chiller | BiQuadratic | EIRRatio | CHWT | OAT | 0.47344 | 0.015708 | -0.000948 | 0.012261 | 9.55e-05 | -0.000352 | [10 empty] | From .dat files included with MASControl2
CentChlrAirCoolEIR-fPLR | Chiller | Quadratic | EIRRatio | PLR |  | coeff_1: 0.24258; coeff_2: 0.41468; coeff_3: 0.34274 | [6 empty] | From .dat files included with MASControl2
CentH2O-Cap-fCHWT&ECT | HermCentrifugal | BiQuadratic | QRatio | CHWT | ECT | 0.36461 | -0.030524 | -0.0019298 | 0.066368 | -0.001892 | 0.0031106 | [10 empty] | From .dat files included with MASControl2
CentH2O-EIR-fCHWT&ECT | HermCentrifugal | BiQuadratic | EIRRatio | CHWT | ECT | 0.65868 | -0.025336 | 0.000991 | 0.012803 | 0.000171 | -0.000301 | [10 empty] | From .dat files included with MASControl2
CentH2O-EIR-fPLR&dT | HermCentrifugal | BiQuadratic | EIRRatio | PLR | dT | 0.2797 | 0.57376 | 0.2569 | -0.010453 | 0.000475 | -0.0063541 | [10 empty] | From .dat files included with MASControl2
CentH2OVSD-Cap-fCHWT&ECT | HermCentrifugal | BiQuadratic | QRatio | CHWT | ECT | 0.36211 | -0.03225 | -0.000886 | 0.066744 | -0.0017315 | 0.0021804 | [10 empty] | From .dat files included with MASControl2
CentH2OVSD-EIR-fCHWT&ECT | HermCentrifugal | BiQuadratic | EIRRatio | CHWT | ECT | 0.41386 | -0.088038 | 0.00098 | 0.05677 | -0.000946 | 0.0014187 | [10 empty] | From .dat files included with MASControl2
CentH2OVSD-EIR-fPLR&dT | HermCentrifugal | BiQuadratic | EIRRatio | PLR | dT | 0.14703 | -0.0034967 | 1.0116 | -0.0064745 | 0.00088 | -0.02096 | [10 empty] | From .dat files included with MASControl2
ChillerCentCapFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
ChillerCentEIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
ChillerCentEIRPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | From Dick Lord's Chiller Model study for ASHRAE 2007 baseline
ChlrAirRecipEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.11444; coeff_2: 0.54593; coeff_3: 0.3423 | 0 | 1 |  |  | 0.11 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirRecipEIRRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.54278 | -0.013907 | 0.000476 | 0.012197 | 0.000149 | -0.000334 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.72 | 1.3 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirRecipQRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 1.126 | 0.041571 | 0.000253 | -0.010526 | 1e-05 | -0.000256 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.82 | 1.3 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrewEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.036487; coeff_2: 0.73474; coeff_3: 0.21995 | 0 | 1 |  |  | 0.04 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrewEIRRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.57062 | 0.011954 | -0.000522 | -3.2e-05 | 0.000421 | -0.000606 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.7 | 1.38 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrewQRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.98596 | 0.049487 | -0.000298 | -0.003737 | -4.5e-05 | -0.000502 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.82 | 1.3 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrollEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.063691; coeff_2: 0.58489; coeff_3: 0.3528 | 0 | 1 |  |  | 0.06 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrollEIRRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.70219 | -0.004466 | 0.000535 | -0.005506 | 0.000544 | -0.000729 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.69 | 1.45 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrAirScrollQRatio_fTchwsToadbSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 1.0214 | 0.037021 | 0.000233 | -0.003893 | -6.5e-05 | -0.000269 |  |  |  |  | 4.44 | 12.22 | 23.89 | 46.11 | 0.82 | 1.3 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrHPAirCoolCap-fCHW&OAT | Chiller | BiQuadratic | QRatio | CHWT | OAT | 1.1308 | 0.03158 | 0.000358 | -0.0098563 | 1.01e-05 | -0.00015 | [10 empty] | From .dat files included with MASControl2
ChlrHPAirCoolEIR-fCHW&OAT | Chiller | BiQuadratic | EIRRatio | CHWT | OAT | 0.56374 | -0.0092259 | 0.000353 | 0.0094522 | 0.000187 | -0.000314 | [10 empty] | From .dat files included with MASControl2
ChlrHPAirHeatCap-fHW&39- | Chiller | BiQuadratic | QRatio | HW | 39 | 0.92142 | -0.0034137 | -3.86e-06 | 0.0324 | 0.000611 | -5.18e-05 | [10 empty] | From .dat files included with MASControl2
ChlrHPAirHeatCap-fHW&39+ | Chiller | BiQuadratic | QRatio | HW | 39+ | 0.94069 | -0.0040359 | 4.21e-07 | 0.046219 | -0.0017032 | -2.27e-07 | [10 empty] | From .dat files included with MASControl2
ChlrHPAirHeatEIR-fHW&39- | Chiller | BiQuadratic | EIRRatio | HW | 39 | 0.33398 | 0.019818 | 1.2e-05 | 0.0048024 | -3.32e-05 | -0.000898 | [10 empty] | From .dat files included with MASControl2
ChlrHPAirHeatEIR-fHW&39+ | Chiller | BiQuadratic | EIRRatio | HW | 39+ | 0.38887 | 0.018107 | 1.94e-05 | -0.026684 | 0.0020567 | -0.000499 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OCoolCap_fCHW&ECT | Chiller/HP | BiQuadratic | QRatio | CHWT | ECT | 35.6836 | 0.62273 | -0.0056779 | -0.24895 | -0.0034613 | 0.011143 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OCoolCap_fCHW&ECT-Old | Chiller/HP | BiQuadratic | QRatio | CHWT | ECT | 0.96601 | 0.040501 | 0.000589 | -0.0080987 | 6.65e-05 | -0.000454 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OCoolEIR_fCHW&ECT | Chiller/HP | BiQuadratic | EIRRatio | CHWT | ECT | 0.11129 | -0.0020946 | 0.000201 | 0.0017053 | 0.000168 | -0.000308 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OCoolEIR_fCHW&ECT-Old | Chiller/HP | BiQuadratic | EIRRatio | CHWT | ECT | 0.61093 | -0.016352 | 0.000407 | 0.0030442 | 0.000592 | -0.000668 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OHeatCap_fHWS&EET | Chiller/HP | BiQuadratic | QRatio | HWS | EET | 29.914 | 0.15443 | -0.0041472 | 0.68325 | -0.0020315 | 0.0019958 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OHeatCap_fHWS&EET-Old | Chiller/HP | BiQuadratic | QRatio | HWS | EET | 0.8465 | -0.0026481 | 2.31e-05 | 0.027001 | 0.00013 | -0.000127 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OHeatEIR_fHWS&EET | Chiller/HP | BiQuadratic | EIRRatio | HWS | EET | 0.12004 | -0.00011232 | 9.85e-05 | -0.0010793 | 7.32e-05 | -0.000134 | [10 empty] | From .dat files included with MASControl2
ChlrHPH2OHeatEIR_fHWS&EET-Old | Chiller/HP | BiQuadratic | EIRRatio | HWS | EET | 0.20682 | 0.018812 | 0.000105 | -0.01266 | 0.000406 | -0.000399 | [10 empty] | From .dat files included with MASControl2
ChlrWtrCentPathAAllEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.22215; coeff_2: 0.50316; coeff_3: 0.2569 | 0.1 | 1 |  |  | 0.28 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathAAllEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.65864 | -0.025339 | 0.000991 | 0.012801 | 0.000171 | -0.000301 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.68 | 1.05 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathAAllQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.36469 | -0.030521 | -0.00193 | 0.066374 | -0.001892 | 0.003111 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.87 | 0.91 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.055483; coeff_2: 0.45187; coeff_3: 0.48824 | 0.1 | 1 |  |  | 0.11 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql300Lt600tonEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.75638 | -0.015019 | 0.000156 | 0.00246 | 0.000515 | -0.000687 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.63 | 1.12 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql300Lt600tonQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 1.3561 | 0.04875 | -0.000888 | -0.014525 | -0.000286 | -4e-05 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.87 | 1.52 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql600tonEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.10743; coeff_2: 0.15677; coeff_3: 0.73935 | 0.1 | 1 |  |  | 0.13 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql600tonEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.73762 | 0.001456 | -0.000223 | 0.007116 | 0.000267 | -0.000735 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.76 | 1.08 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBGtEql600tonQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.85445 | 0.042526 | -0.000185 | 0.011697 | -0.000497 | -0.000412 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.9 | 1.33 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBLt300tonEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.20839; coeff_2: -0.1214; coeff_3: 0.91846 | 0.1 | 1 |  |  | 0.21 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBLt300tonEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.71111 | -0.023515 | 0.001194 | 0.017737 | 0.000152 | -0.001159 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.69 | 1.13 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrCentPathBLt300tonQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 1.1551 | 0.036503 | -0.000499 | -0.001455 | -0.000439 | -0.000172 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.86 | 1.37 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathAAllEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.31096; coeff_2: 0.32252; coeff_3: 0.37274 | 0.1 | 1 |  |  | 0.35 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathAAllEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.66531 | -0.009339 | 0.000483 | 0.009492 | 0.000544 | -0.000864 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.74 | 1.27 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathAAllQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.96744 | 0.037082 | 0.000434 | -0.005837 | -4.9e-05 | -0.000274 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.89 | 1.33 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathBAllEIRRatio_fQRatio | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0; coeff_2: 0.6206; coeff_3: 0.3893 | 0.1 | 1 |  |  | 0.07 |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathBAllEIRRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.42827 | -0.024071 | 0.000849 | 0.016416 | 0.000381 | -0.00059 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.5 | 1.07 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ChlrWtrPosDispPathBAllQRatio_fTchwsTcwsSI | Electric Chiller | BiQuadratic | QRatio | Tchws | Tcws | 0.89993 | 0.030102 | -0.000332 | -0.001743 | -9.2e-05 | 0.000229 |  |  |  |  | 4.44 | 12.22 | 15.56 | 29.44 | 0.93 | 1.21 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CHW-Coil-Cap-fAirflow | CHWCoils | Quadratic | QRatio | Airflow |  | coeff_1: 0.0488; coeff_2: 1.38; coeff_3: -0.425 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
CHW-Coil-Cap-fEWB&EWT | CHWCoils | BiQuadratic | QRatio | EWB | EWT | 1.6727 | -0.13378 | 0.0065124 | 0.038281 | 8.26e-05 | -0.0058689 |  |  |  |  | 15.5556 | 29.4444 | 4.4444 | 18.3333 |  |  | From .dat files included with MASControl2
CHW-Coil-Cap-fFluidFlow | CHWCoils | Quadratic | QRatio | FluidFlow |  | coeff_1: 0.218; coeff_2: 3199.5088; coeff_3: -3280000 | 0 | 1 |  |  |  |  | From .dat files included with MASControl2
Coffin Defrost Curve | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.3475; coeff_2: 0.0296; coeff_3: 0.0007; coeff_4: 3e-05 | -55 | 55 |  |  |  |  | For SuperMarket Prototype Buildings
Coffin Latent Curve | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.3379; coeff_2: 0.0309; coeff_3: 0.0005; coeff_4: 4e-05 | -55 | 55 |  |  |  |  | For SuperMarket Prototype Buildings
COIL-BF-FFLOW-SPEC | CoilBF-FFLOW | Linear |  | Flow |  | coeff_1: 0.33; coeff_2: 1419.6496 |  |  |  |  | 0.8 |  | From .dat files included with MASControl2
Coil-Bypass-Factor-fPLR | CHWCoils | Linear | QRatio | PLR |  | coeff_1: 1; coeff_2: 0 | [6 empty] | From .dat files included with MASControl2
CoilClgDXDblEIRRatio_fCFMRatio | DX Cooling Coil | Cubic | EIRRatio | FlowRatio |  | coeff_1: 1.0079; coeff_2: 0.34544; coeff_3: -0.69229; coeff_4: 0.3389 | 0 | 1 |  |  |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXDblQRatio_fCFMRatio | DX Cooling Coil | Cubic | QRatio | FlowRatio |  | coeff_1: 0.47279; coeff_2: 1.2433; coeff_3: -1.0387; coeff_4: 0.32258 | -100 | 100 | 0.47 |  |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXEIRRatio_fQFrac | DX Cooling Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0; coeff_2: 5.1091; coeff_3: -8.5515; coeff_4: 4.4744 | 0.7 | 1 | 0.92 | 1 |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXEIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.11671 | 0.028458 | -0.000411 | 0.021422 | 0.000162 | -0.00068 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.77 | 1.33 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXQRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.86779 | 0.014245 | 0.000554 | -0.007569 | 3.2e-05 | -0.000191 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.77 | 1.29 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER13EER11EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -0.19999 | -0.035686 | 0.000787 | 0.074834 | -0.000516 | -0.000573 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.55 | 1.44 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER15EER11EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -1.7905 | -0.028777 | 0.000763 | 0.15339 | -0.001482 | -0.000721 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.35 | 1.42 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER16EER13EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.68668 | -0.035826 | 0.000781 | 0.025564 | 0.000163 | -0.000559 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.65 | 1.51 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER17EER11EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -3.0605 | -0.023207 | 0.000744 | 0.21609 | -0.002253 | -0.000839 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.2 | 1.4 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER18EER13EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -1.2471 | -0.027513 | 0.000752 | 0.12112 | -0.001013 | -0.000736 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.41 | 1.48 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEER20EER13EIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -2.7249 | -0.02112 | 0.00073 | 0.19413 | -0.001911 | -0.000872 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.23 | 1.45 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSEEREIRRatio_fQFrac | DX Cooling Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0; coeff_4: 0 | 0.7 | 1 | 1 | 1 |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSnglEIRRatio_fCFMRatio | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.156; coeff_2: -0.1816; coeff_3: 0.0256 | 0 | 1 |  |  |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgDXSnglQRatio_fCFMRatio | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5 |  |  |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgPTACEIRRatio_fQFrac | DX Cooling Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.85; coeff_2: 0.15; coeff_3: 0; coeff_4: 0 | 0.7 | 1 | 0.96 | 1 |  |  | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgPTACEIRRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.34143 | 0.03481 | -0.000625 | 0.004941 | 0.000437 | -0.000729 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.75 | 1.4 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
CoilClgPTACQRatio_fTwbToadbSI | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.94288 | 0.009538 | 0.000684 | -0.011002 | 6e-06 | -1e-05 |  |  |  |  | 13.89 | 25 | 23.89 | 46.11 | 0.71 | 1.34 | From CBECC Appendix_3.7_PerformanceCurves-S901G.xlsx
ConstantCubic |  | Cubic |  |  |  | coeff_1: 1; coeff_2: 0; coeff_3: 0; coeff_4: 0 | -100 | 100 |  |  |  |  | From Reference Buildings
Cool-PLF-fPLR | DX Cooling Coil | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.9095; coeff_2: 0.098648; coeff_3: -0.0081949 | 0 | 1 |  |  |  |  | From PNNL Prototype FullServiceRestaurant
CoolCLennoxStandard10Ton_TGA120S2B_EIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.2055; coeff_2: -0.32953; coeff_3: 0.12308 | 0.75918 | 1.1388 |  |  |  |  | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
Curve_Biquadratic_CBES_01 |  | BiQuadratic |  |  |  | 0.86779 | 0.014245 | 0.000554 | -0.007569 | 3.2e-05 | -0.000191 |  |  |  |  | 0 | 100 | 0 | 100 |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Biquadratic_CBES_02 |  | BiQuadratic |  |  |  | -0.19999 | -0.035686 | 0.000787 | 0.074834 | -0.000516 | -0.000573 |  |  |  |  | 13.9 | 25 | 23.9 | 43.3 |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Biquadratic_CBES_03 |  | BiQuadratic |  |  |  | 0.94259 | 0.0095434 | 0.00068377 | -0.011043 | 5.25e-06 | -9.72e-06 |  |  |  |  | 17 | 22 | 13 | 46 |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Biquadratic_CBES_04 |  | BiQuadratic |  |  |  | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.000728 |  |  |  |  | 17 | 22 | 13 | 46 |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_01 | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_02 | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.156; coeff_2: -0.1816; coeff_3: 0.0256 | 0.5 | 1.5 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_03 |  | Quadratic |  |  |  | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 1 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_04 |  | Quadratic |  |  |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_05 |  | Quadratic |  |  |  | coeff_1: 1.1552; coeff_2: -0.1808; coeff_3: 0.0256 | 0.5 | 1.5 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
Curve_Quadratic_CBES_06 |  | Quadratic |  |  |  | coeff_1: 0.85; coeff_2: 0.15; coeff_3: 0 | 0 | 1 |  |  |  |  | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov
DEER DHW HIR-FPLR Curve | DEERDHWHIR-FPLR | Linear |  | PLR |  | coeff_1: 0; coeff_2: 1 | [6 empty] | From .dat files included with MASControl2
DEER_defrost | Refrigeration | Cubic |  |  |  | coeff_1: 0.023632; coeff_2: 0.0006232; coeff_3: 2.832e-05; coeff_4: 4.4035e-07 | -23 | 7
DEER_Heat_Rejections_LT | Refrigeration | Linear | Capacity | DeltaT |  | coeff_1: 0; coeff_2: 16383.6145 | -100 | 100 |  |  |  |  | From eQuest Grocery store model
DEER_Heat_Rejections_MT | Refrigeration | Linear | Capacity | DeltaT |  | coeff_1: 0; coeff_2: 20626.3421 | -100 | 100 |  |  |  |  | From eQuest Grocery store model
Default_Case_Latent_Cedit_Curve | Refrigeration | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: -6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20
Defrost-ResisDem-Frac-fOWB&ODB | DXCool/Heat | BiLinear | QRatio | OWB | ODB | coeff_1: 0.0333; coeff_2: 0; coeff_3: 0 | -23.333 | 29.444 | -23.333 | 29.444 |  |  | From .dat files included with MASControl2
Defrost-ResisTime-Frac-fOWB&ODB | DXCool/Heat | BiLinear | QRatio | OWB | ODB | coeff_1: 0.0333; coeff_2: 0; coeff_3: 0 | -23.333 | 29.444 | -23.333 | 29.444 |  |  | From .dat files included with MASControl2
Defrost-ReversDem-Frac-fOWB&ODB | DXCool/Heat | BiLinear | QRatio | OWB | ODB | coeff_1: 0.0333; coeff_2: 0; coeff_3: 0 | -23.333 | 29.444 | -23.333 | 29.444 |  |  | From .dat files included with MASControl2
Defrost-ReversTime-Frac-fOWB&ODB | DXCool/Heat | BiLinear | QRatio | OWB | ODB | coeff_1: 0.0583; coeff_2: 0; coeff_3: 0 | -23.333 | 29.444 | -23.333 | 29.444 |  |  | From .dat files included with MASControl2
Desc-Gas-fT&W | Desiccant | BiQuadratic |  | T | W | 18784.3674 | -3209.525 | -11.8831 | 3874.59 | -1.6963 | -23.5318 |  |  |  |  | 7.2222 | 46.1111 | 0 | 0.1 |  |  | From .dat files included with MASControl2
Desc-HR8-fWB1&WB6 | Desiccant | BiQuadratic |  | WB1 | WB6 | -0.27681 | 0.07177 | 0.000735 | 0.14567 | 0.000591 | -0.0026482 |  |  |  |  | 12.7778 | 46.1111 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-HR8PL-fWB1&WB6 | Desiccant | BiQuadratic |  | WB1 | WB6 | -0.052342 | 0.076111 | 0.000502 | 0.11465 | 0.0012353 | -0.0024539 |  |  |  |  | 12.7778 | 46.1111 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-kW-fT&W | Desiccant | BiQuadratic |  | T | W | 3.3302 | -0.010674 | 0 | 0.00404 | 0 | 0 |  |  |  |  | 7.2222 | 46.1111 | 0 | 0.1 |  |  | From .dat files included with MASControl2
Desc-QREG-fWB1&WB6 | Desiccant | BiQuadratic |  | WB1 | WB6 | 80.5807 | -0.62722 | 0.017075 | -2.1862 | 4.37e-05 | 0.018961 |  |  |  |  | 12.7778 | 40.5556 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-QREGPL-fWB1&WB6 | Desiccant | BiQuadratic |  | WB1 | WB6 | 20.309 | -0.15966 | 0.0046008 | -0.58662 | -0.00024 | 0.0052061 |  |  |  |  | 12.7778 | 46.1111 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-T-fT&W | Desiccant | BiQuadratic |  | T | W | 31.5333 | 1.0173 | -0.0033372 | 0.295 | -0.00017 | -0.0015696 |  |  |  |  | 7.2222 | 46.1111 | 0 | 0.1 |  |  | From .dat files included with MASControl2
Desc-T8-fWB1&WB6 | Desiccant | BiLinear |  | WB1 | WB6 | coeff_1: 34.64; coeff_2: 1.6236; coeff_3: 0.2574 | 12.7778 | 46.1111 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-T8PL-fWB1&WB6 | Desiccant | BiLinear |  | WB1 | WB6 | coeff_1: 32.7692; coeff_2: 1.7496; coeff_3: 0.06588 | 12.7778 | 46.1111 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Desc-W-fT&W | Desiccant | BiQuadratic |  | T | W | 7.827 | 0.11938 | 0.01445 | 0.0831 | 0.000697 | 0.002862 |  |  |  |  | 7.2222 | 46.1111 | 0 | 0.1 |  |  | From .dat files included with MASControl2
Direct-Effectiveness-fFlow | EvapCooler | Quadratic |  | Flow |  | coeff_1: 1.18; coeff_2: -546.671; coeff_3: 333000 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DOE Ref DX Clg Coil Cool-CAP-fFlow | DX Cooling Coil | Cubic | QRatio | FlowRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0; coeff_4: 0 | -100 | 100 |  |  |  |  | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-Cap-fT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.97121 | -0.015276 | 0.0014435 | -0.00039321 | -6.8364e-06 | -0.0002906 |  |  |  |  | -100 | 100 | -100 | 100 |  |  | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-EIR-fFlow | DX Cooling Coil | Cubic | EIRRatio | FlowRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0; coeff_4: 0 | -100 | 100 |  |  |  |  | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-EIR-fT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.28687 | 0.023902 | -0.00081065 | 0.013459 | 0.00033894 | -0.000487 |  |  |  |  | -100 | 100 | -100 | 100 |  |  | From DOE Pre-1980 Reference Building
DOE Ref DX Clg Coil Cool-PLF-fPLR | DX Cooling Coil | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.9095; coeff_2: 0.098648; coeff_3: -0.0081949 | 0 | 1
Draft-Fan-EIR-fPLR | FuelBoilers | Cubic | EIRRatio | PLR |  | coeff_1: 0.35071; coeff_2: 0.30805; coeff_3: -0.54137; coeff_4: 0.87199 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DW-Elec-EIR-fPLR | ElecDW-Heater | Linear | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1 | [6 empty] | From .dat files included with MASControl2
DW-Gas-HIR-fPLR | GasDW-Heater | Quadratic |  | PLR |  | coeff_1: 0.021826; coeff_2: 0.97763; coeff_3: 0.000543 | [6 empty] | From .dat files included with MASControl2
DW-Gas-Pilotless-HIR-fPLR | GasDW-Heater | Quadratic |  | PLR |  | coeff_1: 0; coeff_2: 0.99946; coeff_3: 0.000543 | [6 empty] | From .dat files included with MASControl2
DW-HeatPump-Cap-fSupplyT&EDB | HeatPumpDW-Heat | BiQuadratic | QRatio | SupplyT | EDB | 0.74922 | 0 | 0 | 0.02813 | 0.000236 | 0 | [10 empty] | From .dat files included with MASControl2
DW-HeatPump-EIR-fPLR | HeatPumpDW-Heat | Cubic | EIRRatio | PLR |  | coeff_1: 0.085652; coeff_2: 0.93881; coeff_3: -0.18344; coeff_4: 0.15897 | [6 empty] | From .dat files included with MASControl2
DW-HeatPump-EIR-fSupplyT&EDB | HeatPumpDW-Heat | BiQuadratic | EIRRatio | SupplyT | EDB | 1.2531 | 0 | 0 | -0.033921 | 0.000426 | 0 | [10 empty] | From .dat files included with MASControl2
DX Coil Cap-FF | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5 |  |  |  |  | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, OfficeSmall, RetailStandAlone, RetailStripmall, SchoolPrimary, Warehouse
DX-Bypass-Factor-fAirflow | DXCool/Heat | Quadratic | QRatio | Airflow |  | coeff_1: -0.25423; coeff_2: 1.2183; coeff_3: 0.035978 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DX-Bypass-Factor-fEWB&EDB | DXCool/Heat | BiQuadratic | QRatio | EWB | EDB | 0.84631 | 0.014259 | 0.000184 | -0.014792 | -5.48e-06 | 0.000487 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Bypass-Factor-fPLR | DXCool/Heat | Linear | QRatio | PLR |  | coeff_1: 1; coeff_2: 0 | [6 empty] | From .dat files included with MASControl2
DX-Cap-fAirflow | DXCool/Heat | Cubic | QRatio | Airflow |  | coeff_1: 0.064294; coeff_2: 1.9976; coeff_3: -1.4428; coeff_4: 0.38092 | [6 empty] | From .dat files included with MASControl2
DX-Cool-Cap-fEWB&OAT | DXCool/Heat | BiQuadratic | QRatio | EWB | OAT | 0.86792 | 0.014248 | 0.000554 | -0.0075581 | 3.3e-05 | -0.000192 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-Cap-fRPM&OAT | DXCool/Heat | BiQuadratic | QRatio | RPM | OAT | 32 | 9.5493 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-CondFan-fPLR&OAT | DXCool/Heat | BiQuadratic | PwrRatio | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-CycleLoss-fPLR | DXCool/Heat | Linear | QRatio | PLR |  | coeff_1: 0.7; coeff_2: 0.3 | [6 empty] | From .dat files included with MASControl2
DX-Cool-EIR-fEWB&OAT | DXCool/Heat | BiQuadratic | EIRRatio | EWB | OAT | 0.121 | 0.028534 | -0.000411 | 0.021349 | 0.000161 | -0.00068 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-EIR-fPLR | DXCool/Heat | Cubic | EIRRatio | PLR |  | coeff_1: 0.201; coeff_2: -0.0312; coeff_3: 1.95; coeff_4: -1.12 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DX-Cool-EIR-fRPM&OAT | DXCool/Heat | BiQuadratic | EIRRatio | RPM | OAT | 32 | 9.5493 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-Waste-Heat-fEWB&OAT | DXCool/Heat | BiLinear | QRatio | EWB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Cool-Waste-Heat-fRPM&OAT | DXCool/Heat | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
DX-Heat-Cap-fEDB&OAT | DXCool/Heat | BiQuadratic | QRatio | EDB | OAT | 0.74226 | 0 | 0 | 0.030683 | 3.23e-05 | 0 |  |  |  |  | 12.7778 | 29.4444 | -12.2222 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-Cap-fRPM&OAT | DXCool/Heat | BiQuadratic | QRatio | RPM | OAT | 32 | 9.5493 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-CondFan-fPLR&OAT | DXCool/Heat | BiQuadratic | PwrRatio | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-CycleLoss-fPLR | DXCool/Heat | Linear | QRatio | PLR |  | coeff_1: 0.75; coeff_2: 0.25 | [6 empty] | From .dat files included with MASControl2
DX-Heat-EIR-fEDB&OAT | DXCool/Heat | BiQuadratic | EIRRatio | EDB | OAT | 1.254 | 0 | 0 | -0.040063 | 0.0010877 | 0 |  |  |  |  | 12.7778 | 29.4444 | -12.2222 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-EIR-fPLR | DXCool/Heat | Cubic | EIRRatio | PLR |  | coeff_1: 0.0857; coeff_2: 0.939; coeff_3: -0.183; coeff_4: 0.159 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DX-Heat-EIR-fRPM&OAT | DXCool/Heat | BiQuadratic | EIRRatio | RPM | OAT | 32 | 9.5493 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-Waste-Heat-fEDB&OAT | DXCool/Heat | BiLinear | QRatio | EDB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 12.7778 | 29.4444 | -12.2222 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Heat-Waste-Heat-fRPM&OAT | DXCool/Heat | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
DX-Sens-Cap-fAirflow | DXCool/Heat | Cubic | QRatio | Airflow |  | coeff_1: 0.34466; coeff_2: 0.8929; coeff_3: -0.35545; coeff_4: 0.11789 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
DX-Sens-Cap-fEWB&OAT | DXCool/Heat | BiQuadratic | QRatio | EWB | OAT | 2.9322 | -0.09446 | 0.0002 | -0.0071768 | 1.03e-05 | 0.000109 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
DXCOOL-NECB2011-REF-CAPFFLOW | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 1 |  |  |  |  | From NECB 2011
DXCOOL-NECB2011-REF-CAPFT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.86791 | 0.014246 | 0.00055436 | -0.0075575 | 3.3e-05 | -0.0001918 |  |  |  |  | 13 | 24 | 24 | 46 |  |  | From NECB 2011
DXCOOL-NECB2011-REF-COOLEIRFFLOW | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 1 |  |  |  |  | From NECB 2011
DXCOOL-NECB2011-REF-COOLEIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.11694 | 0.028493 | -0.0004112 | 0.021411 | 0.00016103 | -0.0006791 |  |  |  |  | 13 | 24 | 24 | 46 |  |  | From NECB 2011
DXCOOL-NECB2011-REF-COOLPLFFPLR | DX Cooling Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.0277; coeff_2: 4.9151; coeff_3: -8.184; coeff_4: 4.2702 | 0.7 | 1 |  |  |  |  | From NECB, curve modified to take into account how PLF is used in E+, and PLF ranges (> 0.7)
DXHEAT-NECB2011-REF-CAPFFLOW | DX Heating Coil | Cubic | QRatio | FlowRatio |  | coeff_1: 0.84; coeff_2: 0.16; coeff_3: 0; coeff_4: 0 | 0.5 | 1.5 |  |  |  |  | From NECB 2011
DXHEAT-NECB2011-REF-CAPFT | DX Heating Coil | Cubic | QRatio | Toadb |  | coeff_1: 0.729; coeff_2: 0.0319; coeff_3: 0.000136; coeff_4: -8.75e-06 | -20 | 20 |  |  |  |  | From NECB 2011
DXHEAT-NECB2011-REF-EIRFFLOW | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.3824; coeff_2: -0.4336; coeff_3: 0.0512 | 0 | 1 |  |  |  |  | From NECB 2011
DXHEAT-NECB2011-REF-EIRFT | DX Heating Coil | Cubic | EIRRatio | Toadb |  | coeff_1: 1.2183; coeff_2: -0.03612; coeff_3: 0.00142; coeff_4: -2.68e-05 | -20 | 20 |  |  |  |  | From NECB 2011
DXHEAT-NECB2011-REF-PLFFPLR | DX Heating Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.3696; coeff_2: 2.3362; coeff_3: -2.9577; coeff_4: 1.2596 | 0.7 | 1 |  |  |  |  | From NECB 2011
Minisplit-Heat-Cap-fT | DX Heating Coil | BiQuadratic | QRatio | Tiadb | Toadb | 1.1472 | -0.010387 | 0 | 0.0086538 | 0 | 0 |  |  |  |  | -100 | 100 | -100 | 100 |  |  | From OpenStudio-HPXML
Minisplit-Heat-Cap-fFF | DX Heating Coil | Quadratic | QRatio | Tiadb | Toadb | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 2 | 0 | 2 |  |  | From OpenStudio-HPXML
Minisplit-Heat-EIR-fT | DX Heating Coil | BiQuadratic | EIRRatio | Tiadb | Toadb | 0.99999 | 0.0046846 | 5.9013e-05 | -0.0028624 | 1.3041e-05 | -0.00016173 |  |  |  |  | -100 | 100 | -100 | 100 |  |  | From OpenStudio-HPXML
Minisplit-Heat-EIR-fFF | DX Heating Coil | Quadratic | EIRRatio | Tiadb | Toadb | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 2 | 0 | 2 |  |  | From OpenStudio-HPXML
Minisplit-Heat-PLF-fPLR | DX Heating Coil | BiQuadratic | EIRRatio | Tiadb | Toadb | coeff_1: 0.89; coeff_2: 0.11 | 0 | 1 | 0.6 | 1 |  |  | From OpenStudio-HPXML
Minisplit-Cool-Cap-fT | DX Cooling Coil | BiQuadratic | QRatio | Tiadb | Toadb | 0.7532 | 0.0036182 | 0 | 0.0065744 | -6.8718e-05 | 0 |  |  |  |  | 0 | 100 | 0 | 100 |  |  | From OpenStudio-HPXML
Minisplit-Cool-Cap-fFF | DX Cooling Coil | Quadratic | QRatio | Tiadb | Toadb | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 2 | 0 | 2 |  |  | From OpenStudio-HPXML
Minisplit-Cool-EIR-fT | DX Cooling Coil | BiQuadratic | EIRRatio | Tiadb | Toadb | -0.063769 | -0.0013361 | 1.4131e-05 | 0.019433 | -4.914e-05 | -4.9093e-05 |  |  |  |  | 0 | 100 | 0 | 100 |  |  | From OpenStudio-HPXML
Minisplit-Cool-EIR-fFF | DX Cooling Coil | Quadratic | EIRRatio | Tiadb | Toadb | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 0 | 2 | 0 | 2 |  |  | From OpenStudio-HPXML
Minisplit-Cool-PLF-fPLR | DX Cooling Coil | BiQuadratic | EIRRatio | Tiadb | Toadb | coeff_1: 0.89; coeff_2: 0.11 | 0 | 1 | 0.6 | 1 |  |  | From OpenStudio-HPXML
EFG-Si_Spectral-fAirMass | PV-Module | Cubic |  | AirMass |  | coeff_1: 0.93236; coeff_2: 0.055578; coeff_3: -0.0072378; coeff_4: 0.00016577 | [6 empty] | From .dat files included with MASControl2
Elec-HW-Blr-EIR-fPLR | ElecBoilers | Linear | EIRRatio | PLR |  | coeff_1: 0.02; coeff_2: 0.98 | [6 empty] | From .dat files included with MASControl2
Elec-Stm-Blr-EIR-fPLR | ElecBoilers | Linear | EIRRatio | PLR |  | coeff_1: 0.03; coeff_2: 0.97 | [6 empty] | From .dat files included with MASControl2
Engine-Chlr-Cap-fCHWT&ECT | EngineChiller | BiQuadratic | QRatio | CHWT | ECT | 1.0225 | 0.033624 | 0 | -0.0083759 | 0 | 0 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Engine-Chlr-HeatRej-fECT | EngineChiller | Cubic |  | ECT |  | coeff_1: 0.81658; coeff_2: 0.0062293; coeff_3: 0; coeff_4: 0 | 60 | 150 |  |  |  |  | From .dat files included with MASControl2
Engine-Chlr-HeatRej-fPLR | EngineChiller | Cubic |  | PLR |  | coeff_1: 1.0527; coeff_2: -0.052699; coeff_3: 0; coeff_4: 0 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Engine-Chlr-HIR-fCHWT&ECT | EngineChiller | BiQuadratic |  | CHWT | ECT | 0.76856 | -0.01662 | 0.0011635 | 0.0074511 | 0.000302 | -0.000971 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Engine-Chlr-HIR-fPLR | EngineChiller | Quadratic |  | PLR |  | coeff_1: 0.12572; coeff_2: 0.34714; coeff_3: 0.52714 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Engine-Exh-fPLR | EngineGenerator | Quadratic |  | PLR |  | coeff_1: 0.024516; coeff_2: 0.33239; coeff_3: 0.6431 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Engine-HIR-fPLR | EngineGenerator | Linear |  | PLR |  | coeff_1: 0.107; coeff_2: 0.893 | [6 empty] | From .dat files included with MASControl2
Engine-Jac-fPLR | EngineGenerator | Quadratic |  | PLR |  | coeff_1: 0.28794; coeff_2: 1.0205; coeff_3: -0.30839 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
FluidCooler-FluidCap-fApp&WB | FluidCooler | BiQuadratic | QRatio | App | WB | -0.16464 | 0.048677 | -0.0014373 | 0.072275 | 0.000924 | 0.0050854 | [10 empty] | From .dat files included with MASControl2
FluidCooler-FluidCap-fRng&WB | FluidCooler | BiQuadratic | QRatio | Rng | WB | 0 | 0.18 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
ForcedDraft-Blr-HIR-fPLR | FuelBoilers | Quadratic |  | PLR |  | coeff_1: 0.016; coeff_2: 0.94495; coeff_3: 0.039047 | [6 empty] | From .dat files included with MASControl2
ForCurve w Dischrg Dampers FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.19067; coeff_2: 0.31; coeff_3: 0.5 |  |  |  |  | 0.22 | 1 | From .dat files included with MASControl2
ForCurve w Inlet Vanes FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.33962; coeff_2: -0.84814; coeff_3: 1.4957 |  |  |  |  | 0.22 | 1 | From .dat files included with MASControl2
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.1952; coeff_2: -0.30614; coeff_3: 0.11097 | 0.75 | 1.25 |  |  |  |  | From PNNL OfficeMedium
FURNACE_PACU_VAV_CoolCCarrier48TM014_12tons_EIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | -0.53616 | 0.10514 | -0.0017266 | 0.014985 | 0.00065995 | -0.0017385 |  |  |  |  | 16.5556 | 22.1111 | 23.7778 | 47.66 |  |  | From PNNL Prototype Buildings OfficeMedium
FURNACE-EFFPLR-NECB2011 | Gas Heating Coil | Cubic | FIRRatio | QRatio |  | coeff_1: 0.7277; coeff_2: 1.0667; coeff_3: -1.5174; coeff_4: 0.7282 | 0 | 1 |  |  |  |  | From NECB 2011
Furnace-HIR-fPLR | Furnace | Quadratic | FIRRatio | PLR |  | coeff_1: 0.0186; coeff_2: 1.09; coeff_3: -0.113 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Gas-Absor-Cap-fCHWT&ECT | Chiller/Heater | BiQuadratic | QRatio | CHWT | ECT | 0.36207 | 0.0001386 | 0.001458 | 0.073388 | -0.0020606 | 0.00101 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Gas-Absor-HCap-fCoolPLR | Chiller/Heater | Quadratic | QRatio | CoolPLR |  | coeff_1: 0.8636; coeff_2: -1.305; coeff_3: 0.44135 | [6 empty] | From .dat files included with MASControl2
Gas-Absor-HIR-fCHWT&ECT | Chiller/Heater | BiQuadratic |  | CHWT | ECT | 0.96182 | -0.05071 | 0.0031555 | 0.0057328 | 0.000349 | -0.0011852 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Gas-Absor-HIR-fDesiccantT | Chiller/Heater | Cubic |  | DesiccantT |  | coeff_1: 0.85427; coeff_2: 0.0029975; coeff_3: 4.26e-05; coeff_4: 0 | 100 | 300 |  |  |  |  | From .dat files included with MASControl2
Gas-Absor-Qreg-fDesiccantT | Chiller/Heater | Cubic |  | DesiccantT |  | coeff_1: 0.5984; coeff_2: -0.00234; coeff_3: 0; coeff_4: 0 | 100 | 300 |  |  |  |  | From .dat files included with MASControl2
GasTurbine-Cap-fPLR | GasTurbineGen | Linear | QRatio | PLR |  | coeff_1: 1.24; coeff_2: -0.0041 | [6 empty] | From .dat files included with MASControl2
GasTurbine-Exh-fPLR | GasTurbineGen | Quadratic |  | PLR |  | coeff_1: 0.29563; coeff_2: 0.49302; coeff_3: 0.21135 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
GasTurbine-HIR-fPLR | GasTurbineGen | Quadratic |  | PLR |  | coeff_1: 0.44298; coeff_2: 0.3974; coeff_3: 0.15696 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
GHP-Bypass-Factor-fAirflow | GasHeat-Pump | Quadratic | QRatio | Airflow |  | coeff_1: -0.254; coeff_2: 1.22; coeff_3: 0.036 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
GHP-Bypass-Factor-fEWB&EDB | GasHeat-Pump | BiQuadratic | QRatio | EWB | EDB | 0.85028 | 0.014257 | 0.000184 | -0.014792 | -5.48e-06 | 0.000487 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Bypass-Factor-fPLR | GasHeat-Pump | Linear | QRatio | PLR |  | coeff_1: 1; coeff_2: 0 | [6 empty] | From .dat files included with MASControl2
GHP-Cool-Cap-fEWB&OAT | GasHeat-Pump | BiLinear | QRatio | EWB | OAT | coeff_1: 1.1688; coeff_2: 0.01926; coeff_3: -0.01539 | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Cool-Cap-fRPM&OAT | GasHeat-Pump | BiQuadratic | QRatio | RPM | OAT | -372.736 | -234.1297 | -36.658 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Cool-CondFan-fPLR&OAT | GasHeat-Pump | BiQuadratic |  | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Cool-CycleLoss-fPLR | GasHeat-Pump | Linear | QRatio | PLR |  | coeff_1: 0.82; coeff_2: 0.18 | [6 empty] | From .dat files included with MASControl2
GHP-Cool-HIR-fEWB&OAT | GasHeat-Pump | BiQuadratic |  | EWB | OAT | 1.1387 | -0.049248 | 0.000914 | 0.021289 | 0.000306 | -0.000953 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Cool-HIR-fRPM&OAT | GasHeat-Pump | BiQuadratic |  | RPM | OAT | -369.606 | -234.0533 | -36.9316 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Cool-Waste-Heat-fEWB&OAT | GasHeat-Pump | BiLinear | QRatio | EWB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | [6 empty] | From .dat files included with MASControl2
GHP-Cool-Waste-Heat-fRPM&OAT | GasHeat-Pump | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Defrost-Frac-fOWB&ODB | GasHeat-Pump | BiLinear | QRatio | OWB | ODB | coeff_1: 0.0333; coeff_2: 0; coeff_3: 0 | -23.3333 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-Cap-fEDB&OAT | GasHeat-Pump | BiQuadratic | QRatio | EDB | OAT | 0.82916 | 0 | 0 | 0.018171 | 0.000281 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-Cap-fRPM&OAT | GasHeat-Pump | BiQuadratic | QRatio | RPM | OAT | 157.86 | 89.1713 | 12.5841 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-CondFan-fPLR&OAT | GasHeat-Pump | BiQuadratic |  | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-CycleLoss-fPLR | GasHeat-Pump | Linear | QRatio | PLR |  | coeff_1: 0.82; coeff_2: 0.18 | [6 empty] | From .dat files included with MASControl2
GHP-Heat-HIR-fEDB&OAT | GasHeat-Pump | BiQuadratic |  | EDB | OAT | 1.149 | 0 | 0 | -0.017395 | -2.6e-05 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-HIR-fRPM&OAT | GasHeat-Pump | BiQuadratic |  | RPM | OAT | 194.037 | 109.7883 | 15.5021 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-Waste-Heat-fEDB&OAT | GasHeat-Pump | BiLinear | QRatio | EDB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
GHP-Heat-Waste-Heat-fRPM&OAT | GasHeat-Pump | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
GHP-Sens-Cap-fEWB&OAT | GasHeat-Pump | BiQuadratic | QRatio | EWB | OAT | 1.4964 | 0.079057 | -0.004212 | -0.030189 | 0.000157 | 0.00062 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Glass Door Defrost Curve | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.3475; coeff_2: 0.0296; coeff_3: 0.0007; coeff_4: 3e-05 | -55 | 55 |  |  |  |  | For SuperMarket Prototype Buildings
Glass Door Latent Curve | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.3379; coeff_2: 0.0309; coeff_3: 0.0005; coeff_4: 4e-05 | -55 | 55 |  |  |  |  | For SuperMarket Prototype Buildings
GoodCyclingAC-EIR-fPLR | CyclingAC | Cubic | EIRRatio | PLR |  | coeff_1: 2.73e-06; coeff_2: 1.0526; coeff_3: -0.055209; coeff_4: 0.0026224 | [6 empty] | From .dat files included with MASControl2
GSHP/WLHP_BF_fAirflow-Old | GSHP/WLHPCurves | Cubic | QRatio | Airflow |  | coeff_1: -0.828; coeff_2: 14.3; coeff_3: -21.9; coeff_4: 9.4 | [6 empty] | From .dat files included with MASControl2
GSHP/WLHP_BF_fEwbEwt | GSHP/WLHPCurves | BiLinear | QRatio | EWB | EWT | coeff_1: -0.2016; coeff_2: 0.0297; coeff_3: 0.02646 |  |  |  |  | 0.34736 | 1.6734 | From .dat files included with MASControl2
GSHP/WLHP_BF_fEwbEwt-Old | GSHP/WLHPCurves | BiQuadratic | QRatio | EWB | EWT | -5.5227 | 0.73577 | -0.0185 | 0.14188 | 0.000943 | -0.010206 | [10 empty] | From .dat files included with MASControl2
GSHP/WLHP_Cool_Cap_fEwbEwt | GSHP/WLHPCurves | BiLinear | QRatio | EWB | EWT | coeff_1: 0.88114; coeff_2: 0.015264; coeff_3: -0.0074934 |  |  |  |  | 0.80341 | 1.1856 | From .dat files included with MASControl2
GSHP/WLHP_Cool_EIR_fEwbEwt | GSHP/WLHPCurves | BiLinear | EIRRatio | EWB | EWT | coeff_1: 0.41112; coeff_2: -0.00396; coeff_3: 0.030112 |  |  |  |  | 0.30067 | 1.8063 | From .dat files included with MASControl2
GSHP/WLHP_H/C_EIR-fPLR | GSHP/WLHPCurves | Quadratic | EIRRatio | PLR |  | coeff_1: 0.0414; coeff_2: 0.328; coeff_3: 0.57534 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
GSHP/WLHP_H/C_EIR-fPLR-Old | GSHP/WLHPCurves | Cubic | EIRRatio | PLR |  | coeff_1: 0.00988; coeff_2: 1.08; coeff_3: -0.105; coeff_4: 0.0151 | [6 empty] | From .dat files included with MASControl2
GSHP/WLHP_Heat_Cap_fEdbEwt | GSHP/WLHPCurves | BiLinear | QRatio | EDB | EWT | coeff_1: 1.0726; coeff_2: -0.003564; coeff_3: 0.027 |  |  |  |  | 0.96628 | 1.8637 | From .dat files included with MASControl2
GSHP/WLHP_Heat_EIR_fEdbEwt | GSHP/WLHPCurves | BiLinear | EIRRatio | EDB | EWT | coeff_1: 0.59444; coeff_2: 0.01908; coeff_3: -0.009774 |  |  |  |  | 0.68192 | 1.1029 | From .dat files included with MASControl2
HeatSys1 Boiler Non-Condensing Boiler Curve | Boiler | Cubic | FIRRatio | QRatio |  | coeff_1: 0.62643; coeff_2: 0.64564; coeff_3: -0.77721; coeff_4: 0.31381 | 0.1 | 1 |  |  |  |  | From Prototype Buildings
HeatWheel-EIR-fSpeed | ERVUnit | Linear | EIRRatio | Speed |  | coeff_1: 25.8; coeff_2: 7.6394 | [6 empty] | From .dat files included with MASControl2
Herm-Cent-Cap-fCHWT&ECT | HermCentrifugal | BiQuadratic | QRatio | CHWT | ECT | 0.2579 | 0.038902 | -0.000217 | 0.046868 | -0.000943 | -0.000343 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Herm-Cent-EIR-fCHWT&ECT | HermCentrifugal | BiQuadratic | EIRRatio | CHWT | ECT | 0.93388 | -0.058212 | 0.0045004 | 0.00243 | 0.000486 | -0.001215 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Herm-Cent-EIR-fPLR | HermCentrifugal | Quadratic | EIRRatio | PLR |  | coeff_1: 0.2229; coeff_2: 0.31339; coeff_3: 0.46371 | 0 | 0.105 |  |  |  |  | From .dat files included with MASControl2
Herm-Rec-Cap-fCHWT&ECT | HermReciprocatg | BiQuadratic | QRatio | CHWT | ECT | 0.50788 | 0.14523 | -0.0062564 | -0.0011178 | -0.00013 | -0.000282 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Herm-Rec-EIR-fCHWT&ECT | HermReciprocatg | BiQuadratic | EIRRatio | CHWT | ECT | 1.0308 | -0.10354 | 0.0071021 | 0.0093186 | 0.000318 | -0.00104 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Herm-Rec-EIR-fPLR | HermReciprocatg | Quadratic | EIRRatio | PLR |  | coeff_1: 0.088065; coeff_2: 1.1377; coeff_3: -0.22581 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Hospital Kitchen_Flr_5_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.0236; coeff_2: 0.0006; coeff_3: 0; coeff_4: 0 | -35 | 20 |  |  |  |  | From Prototype Buildings
Hospital Kitchen_Flr_5_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: 6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20 |  |  |  |  | From Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.0236; coeff_2: 0.0006; coeff_3: 0; coeff_4: 0 | -35 | 20 |  |  |  |  | From Prototype Buildings
HotelLarge Kitchen_Flr_6_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: 6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20 |  |  |  |  | From Prototype Buildings
HP-Bypass-Factor-fAirflow | Water-LoopHP | Cubic | QRatio | Airflow |  | coeff_1: -0.828; coeff_2: 14.3; coeff_3: -21.9; coeff_4: 9.4 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
HP-Bypass-Factor-fEWB&EWT | Water-LoopHP | BiQuadratic | QRatio | EWB | EWT | -5.5227 | 0.73577 | -0.0185 | 0.14188 | 0.000943 | -0.010206 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HP-Cool-Cap-fEWB&EWT | Water-LoopHP | BiQuadratic | QRatio | EWB | EWT | 0.38054 | 0.041974 | -3.09e-05 | -0.0066429 | 2.28e-05 | -8.81e-05 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HP-Cool-EIR-fEWB&EWT | Water-LoopHP | BiQuadratic | EIRRatio | EWB | EWT | 1.3258 | -0.05045 | 0.000988 | 0.020364 | 7.91e-05 | -0.000531 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HP-Cool-EIR-fPLR | Water-LoopHP | Linear | EIRRatio | PLR |  | coeff_1: 0.125; coeff_2: 0.875 | [6 empty] | From .dat files included with MASControl2
HP-Heat-Cap-fEDB&EWT | Water-LoopHP | BiLinear | QRatio | EDB | EWT | coeff_1: 0.72324; coeff_2: -0.012204; coeff_3: 0.02538 | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HP-Heat-EIR-fEDB&EWT | Water-LoopHP | BiLinear | EIRRatio | EDB | EWT | coeff_1: 1.2124; coeff_2: 0.01089; coeff_3: -0.02088 | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HP-Heat-EIR-fPLR | Water-LoopHP | Cubic | EIRRatio | PLR |  | coeff_1: 0.0857; coeff_2: 0.939; coeff_3: -0.183; coeff_4: 0.15897 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
HP-Sens-Cap-fAirflow | Water-LoopHP | Cubic | QRatio | Airflow |  | coeff_1: -0.13; coeff_2: 2.16; coeff_3: -1.6; coeff_4: 0.573 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
HP-Sens-Cap-fEWB&EWT | Water-LoopHP | BiQuadratic | QRatio | EWB | EWT | 1.6832 | 0.01241 | -0.0021578 | -0.0092511 | 6.32e-05 | 0.000174 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
HPACCoolCapFFF | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5
HPACCoolCapFT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 |  |  |  |  | 12.7778 | 23.8889 | 21.1111 | 46.1111
HPACCOOLEIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.156; coeff_2: -0.1816; coeff_3: 0.0256 | 0.5 | 1.5
HPACCOOLEIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 |  |  |  |  | 12.7778 | 23.8889 | 21.1111 | 46.1111
HPACCOOLPLFFPLR | DX Cooling Coil | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.85; coeff_2: 0.15; coeff_3: 0 | 0 | 1
HPACHeatCapFFF | DX Heating Coil | Cubic | QRatio | FlowRatio |  | coeff_1: 0.84; coeff_2: 0.16; coeff_3: 0; coeff_4: 0 | 0.5 | 1.5 |  |  |  |  | From Prototype Buildings
HPACHeatCapFT | DX Heating Coil | Cubic | QRatio | Toadb |  | coeff_1: 0.75875; coeff_2: 0.027626; coeff_3: 0.00014872; coeff_4: 3.4992e-06 | -20 | 20 |  |  |  |  | From Prototype Buildings
HPACHeatEIRFFF | DX Heating Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.3824; coeff_2: -0.4336; coeff_3: 0.0512 | 0 | 1 |  |  |  |  | From Prototype Buildings
HPACHeatEIRFT | DX Heating Coil | Cubic | EIRRatio | Toadb |  | coeff_1: 1.1925; coeff_2: -0.030044; coeff_3: 0.0010375; coeff_4: -2.3328e-05 | -20 | 20 |  |  |  |  | From Prototype Buildings
Htrec-Chlr-Cap-fCHWT&ECT | ElecHeatRecover | BiQuadratic | QRatio | CHWT | ECT | 0.2579 | 0.038902 | -0.000217 | 0.046868 | -0.000943 | -0.000343 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 51.6667 |  |  | From .dat files included with MASControl2
Htrec-Chlr-EIR-fCHWT&ECT | ElecHeatRecover | BiQuadratic | EIRRatio | CHWT | ECT | 0.93388 | -0.058212 | 0.0045004 | 0.00243 | 0.000486 | -0.001215 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 51.6667 |  |  | From .dat files included with MASControl2
Htrec-Chlr-EIR-fPLR | ElecHeatRecover | Quadratic | EIRRatio | PLR |  | coeff_1: 0.34903; coeff_2: 0.26387; coeff_3: 0.3871 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Htrej-Fan-Pwr-fDamper | FluidCooler | Cubic |  | Damper |  | coeff_1: 0.37608; coeff_2: -0.21441; coeff_3: 1.0054; coeff_4: -0.16712 |  |  |  |  | 0.36 | 1 | From .dat files included with MASControl2
HW-Coil-Cap-fAirflow | HWCoils | Quadratic | QRatio | Airflow |  | coeff_1: 0.289; coeff_2: 1.03; coeff_3: -0.317 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
HW-Coil-Cap-fdT | HWCoils | Quadratic | QRatio | dT |  | coeff_1: -0.00467; coeff_2: 1.8; coeff_3: 0.01096 | 0 | 150 |  |  | 0.01 |  | From .dat files included with MASControl2
HW-Coil-Cap-fFluidFlow | HWCoils | Quadratic | QRatio | FluidFlow |  | coeff_1: 0.18; coeff_2: 2945.2432; coeff_3: -2540000 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Indirect-Effectiveness-fFlow | EvapCooler | Quadratic |  | Flow |  | coeff_1: 1.1; coeff_2: -350; coeff_3: 306000 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Inverter_EIR-fPLR | PV-Inverter | Quadratic | EIRRatio | PLR |  | coeff_1: 0.016778; coeff_2: 1.0377; coeff_3: -0.054444 | [6 empty] | From .dat files included with MASControl2
Large-CHW-Bypass-fAirflow | CHWCoils | Quadratic | QRatio | Airflow |  | coeff_1: 0.397; coeff_2: 0.15; coeff_3: 0.45375 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Large-CHW-Coil-Bypass-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | 0.43594 | 0.23652 | -0.0047628 | -0.13303 | 0.0011956 | 0.000859 |  |  |  |  | 15.5556 | 29.4444 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Large-CHW-Coil-Cap-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | 0.097932 | -0.13886 | 0.012442 | 0.088907 | 0.0019389 | -0.0093056 |  |  |  |  | 15.5556 | 29.4444 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Large-CHW-Sens-Cap-fAirflow | CHWCoils | Quadratic | QRatio | Airflow |  | coeff_1: 0.202; coeff_2: 0.855; coeff_3: -0.057 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Large-CHW-Sens-Cap-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | 0.12077 | -0.12456 | 0.0063828 | 0.11146 | 0.0018479 | -0.0065083 |  |  |  |  | 15.5556 | 13.3333 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Lp2Lp_Cap_fCHW&HWR | Loop2Loop | BiQuadratic | QRatio | CHWT | HWR | 0.95122 | 0.035393 | 0.00027 | -0.0026541 | -8.69e-05 | -0.000274 | [10 empty] | From .dat files included with MASControl2
Lp2Lp_EIR_fCHW&HWR | Loop2Loop | BiQuadratic | EIRRatio | CHWT | HWR | 0.59919 | -0.0095072 | 0.000335 | 0.0086388 | 0.000312 | -0.000386 | [10 empty] | From .dat files included with MASControl2
Lp2Lp-EIR-fPLR-1Comp/Ckt | Loop2Loop | Quadratic | EIRRatio | PLR |  | coeff_1: 0.034811; coeff_2: 0.95945; coeff_3: 0.0057349 | [6 empty] | From .dat files included with MASControl2
Lp2Lp-EIR-fPLR-2Comp/Ckt | Loop2Loop | Quadratic | EIRRatio | PLR |  | coeff_1: 0.022977; coeff_2: 0.9015; coeff_3: 0.075518 | [6 empty] | From .dat files included with MASControl2
LT_compressor_capacity | Refrigeration | BiCubic | Capacity | Suction T | Discharge T | 170751.834 | 6102.9037 | 78.262 | -2959.4326 | 19.7877 | -90.9581 | 0.43596 | -0.041158 | -0.60885 | 0.45913 | -40 | 17.8 | 4.4 | 54.4 |  |  | From AEDG
LT_compressor_power | Refrigeration | BiCubic | Power | Suction T | Discharge T | 29669.2711 | 1027.632 | 18.1066 | -442.1997 | 11.1335 | -20.3805 | 0.13998 | -0.058867 | -0.21845 | 0.20386 | -40 | -17.8 | 4.4 | 54.4 |  |  | From AEDG
mc-Si_Spectral-fAirMass | PV-Module | Cubic |  | AirMass |  | coeff_1: 0.96113; coeff_2: 0.0282; coeff_3: -0.0013458; coeff_4: -0.00012036 | [6 empty] | From .dat files included with MASControl2
Measured_CoolCStandard10Ton_EIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.192; coeff_2: -0.1917; coeff_3: 0 | 0.776 | 1.197 |  |  |  |  | From PNNL Prototype FullServiceRestaurant
MNECB-CAP-FAPP&WB | CAP-FAPP&WB | BiQuadratic | QRatio | App | WB | -0.054256 | -0.063982 | 0.026052 | 0.26002 | 0.00080909 | 0.015904 | [10 empty] | From .dat files included with MASControl2
MNECB-CAP-FRNG&WB | CAP-FRNG&WB | BiQuadratic | QRatio | Rng | WB | 188.8588 | 0.30023 | -0.045692 | 35.4084 | 0.60135 | 0.78576 | [10 empty] | From .dat files included with MASControl2
MNECB-Centrif-CAP-FT | Centrif-CAP-FT | BiQuadratic | QRatio | T | T | 0.70791 | -0.0020066 | -0.002596 | 0.030059 | -0.0010564 | 0.0020457 | [10 empty] | From .dat files included with MASControl2
MNECB-Centrif-EIR-FPLR | Centrif-EIR-FPLR | Quadratic | EIRRatio | PLR |  | coeff_1: 0.17149; coeff_2: 0.5882; coeff_3: 0.23737 | [6 empty] | From .dat files included with MASControl2
MNECB-Centrif-EIR-FT | Centrif-EIR-FT | BiQuadratic | EIRRatio | T | T | 0.56054 | -0.013779 | 6.57e-05 | 0.013219 | 0.0002686 | -0.00050113 | [10 empty] | From .dat files included with MASControl2
MNECB-DW-HIR-fPLR | DHW-HIR | Quadratic |  | PLR |  | coeff_1: 0.021826; coeff_2: 0.97763; coeff_3: 0.000543 | [6 empty] | From .dat files included with MASControl2
MNECB-HW-HIR-fPLR | HW-HIR | Quadratic |  | PLR |  | coeff_1: 0.082597; coeff_2: 0.99676; coeff_3: -0.079361 | [6 empty] | From .dat files included with MASControl2
MNECB-Recip-CAP-FT | Recip-CAP-FT | BiQuadratic | QRatio | T | T | 1.0303 | 0.03347 | 0.00023639 | -0.0072959 | -2.32e-05 | -0.00014894 | [10 empty] | From .dat files included with MASControl2
MNECB-Recip-EIR-FPLR | Recip-EIR-FPLR | Quadratic | EIRRatio | PLR |  | coeff_1: 0.081441; coeff_2: 0.41927; coeff_3: 0.4994 | [6 empty] | From .dat files included with MASControl2
MNECB-Recip-EIR-FT | Recip-EIR-FT | BiQuadratic | EIRRatio | T | T | 0.4997 | -0.013084 | 0.00026642 | 0.016593 | 0.00018539 | -0.00037565 | [10 empty] | From .dat files included with MASControl2
Multi Shelf Vertical Latent Energy Multiplier | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: -6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20 |  |  |  |  | From Reference Buildings
Multi Zone VAV with Airfoil or Backward Incline riding the curve | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.1631; coeff_2: 1.5901; coeff_3: -0.8817; coeff_4: 0.1281 | 0 | 1 |  |  | 0.7 |  | From ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi Zone VAV with Airfoil or Backward Incline with inlet vanes | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.9977; coeff_2: -0.659; coeff_3: 0.9547; coeff_4: -0.2936 | 0 | 1 |  |  | 0.5 |  | From ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi Zone VAV with Forward Curved fans riding the curve | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.1224; coeff_2: 0.612; coeff_3: 0.5983; coeff_4: -0.3334 | 0 | 1 |  |  | 0.3 |  | From ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi Zone VAV with Forward Curved with inlet vanes | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.3038; coeff_2: -0.7608; coeff_3: 2.2729; coeff_4: -0.8169 | 0 | 1 |  |  | 0.3 |  | From ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi zone VAV with static pressure reset | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.04076; coeff_2: 0.088045; coeff_3: -0.072926; coeff_4: 0.94374 | 0 | 1 |  |  | 0.1 |  | OpenStudio default, baseline for System Types 5-8 from ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi Zone VAV with vane-axial with variable pitch blades | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.1639; coeff_2: -0.4016; coeff_3: 1.9909; coeff_4: -0.7541 | 0 | 1 |  |  | 0.2 |  | From ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Multi Zone VAV with VSD and fixed SP setpoint | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.0013; coeff_2: 0.147; coeff_3: 0.9506; coeff_4: -0.0998 | 0 | 1 |  |  | 0.2 |  | Appendix G baseline from ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
New_Low_Temp_Comp_Cap_Curve |  | BiCubic |  |  |  | 58336.861 | 1561.7435 | 6.6068 | -283.6501 | -0.12023 | -12.4957 | -0.11628 | 0.002277 | -0.11815 | 0.03284 | -40 | -17.8 | 4.4 | 54.4
New_Low_Temp_Comp_Pwr_Curve |  | BiCubic |  |  |  | 6274.9904 | 61.3907 | 1.6209 | 129.1128 | 0.87412 | 1.9581 | 0.030293 | 0.0057547 | 0.004654 | -0.00074991 | -40 | -17.8 | 4.4 | 54.4
New_Med_Temp_Comp_Cap_Curve |  | BiCubic |  |  |  | 61412.175 | 1570.8519 | 13.5334 | -500.1952 | 8.1639 | -3.6895 | 0.054486 | -0.088097 | 0.0063816 | -0.037503 | -23.3 | 7.2 | 10 | 60
New_Med_Temp_Comp_Pwr_Curve |  | BiCubic |  |  |  | 4994.0336 | 170.2497 | 2.8464 | 356.794 | -6.3075 | -1.4099 | 0.01216 | 0.076232 | -0.057527 | 0.0090544 | -23.3 | 7.2 | 10 | 60
No SP Reset VSD Fan | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.070429; coeff_2: 0.38533; coeff_3: -0.46086; coeff_4: 1.0092 | 0 | 1 |  |  | 0.1 |  | From California Energy Commision, "Advanced Variable Air Volume System Design Guide," October 2004
Old_Low_Temp_Comp_Cap_Curve |  | BiCubic |  |  |  | 170751.834 | 6102.9037 | 78.262 | -2959.4327 | 19.7877 | -90.9581 | 0.43596 | -0.041158 | -0.60885 | 0.45913 | -40 | -17.8 | 4.4 | 54.4
Old_Low_Temp_Comp_Pwr_Curve |  | BiCubic |  |  |  | 29669.2711 | 1027.632 | 18.1066 | -442.1997 | 11.1335 | -20.3805 | 0.13998 | -0.058867 | -0.21845 | 0.20386 | -40 | -17.8 | 4.4 | 54.4
Old_Med_Temp_Comp_Cap_Curve |  | BiCubic |  |  |  | 151166.436 | 5266.3479 | 60.6727 | -1851.5594 | 5.7313 | -46.9277 | 0.1364 | -0.035698 | -0.40305 | -0.03929 | -23.3 | 7.2 | 10 | 60
Old_Med_Temp_Comp_Pwr_Curve |  | BiCubic |  |  |  | 7438.9223 | -269.5976 | -9.8561 | 553.5733 | -3.3859 | 14.8658 | -0.1008 | 0.0098228 | 0.097362 | -0.039675 | -23.3 | 7.2 | 10 | 60
Open Latent Curve | Refrigerated Case | Cubic |  |  |  | coeff_1: -0.0187; coeff_2: 0.0458; coeff_3: 0.0011; coeff_4: 5e-05 | -55 | 55 |  |  |  |  | For SuperMarket Prototype Buildings
Open-Cent-Cap-fCHWT&ECT | OpenCentrifugal | BiQuadratic | QRatio | CHWT | ECT | 0.2579 | 0.038902 | -0.000217 | 0.046868 | -0.000943 | -0.000343 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Open-Cent-EIR-fCHWT&ECT | OpenCentrifugal | BiQuadratic | EIRRatio | CHWT | ECT | 0.93388 | -0.058212 | 0.0045004 | 0.00243 | 0.000486 | -0.001215 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Open-Cent-EIR-fPLR | OpenCentrifugal | Quadratic | EIRRatio | PLR |  | coeff_1: 0.2229; coeff_2: 0.31339; coeff_3: 0.46371 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Open-Rec-Cap-fCHWT&ECT | OpenReciprocatg | BiQuadratic | QRatio | CHWT | ECT | 0.50788 | 0.14523 | -0.0062564 | -0.0011178 | -0.00013 | -0.000282 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Open-Rec-EIR-fCHWT&ECT | OpenReciprocatg | BiQuadratic | EIRRatio | CHWT | ECT | 1.0308 | -0.10354 | 0.0071021 | 0.0093186 | 0.000318 | -0.00104 |  |  |  |  | 4.4444 | 18.3333 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Open-Rec-EIR-fPLR | OpenReciprocatg | Quadratic | EIRRatio | PLR |  | coeff_1: 0.088065; coeff_2: 1.1377; coeff_3: -0.22581 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
OpenTwr-FluidCap-fApp&WB | OpenTower | BiQuadratic | QRatio | App | WB | 0.11736 | 0.010589 | 0.000701 | 0.05244 | 0.000724 | 0.0034379 | [10 empty] | From .dat files included with MASControl2
OpenTwr-FluidCap-fRng&WB | OpenTower | BiQuadratic | QRatio | Rng | WB | 0.11662 | 0.20245 | -0.0044014 | -0.015923 | 0.000101 | -0.0011016 | [10 empty] | From .dat files included with MASControl2
PoorCyclingAC-EIR-fPLR | CyclingAC | Cubic | EIRRatio | PLR |  | coeff_1: 0.00036252; coeff_2: 1.3257; coeff_3: -0.4076; coeff_4: 0.081819 | [6 empty] | From .dat files included with MASControl2
PSZ-AC DX Coil EIR-FT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 |  |  |  |  | 12.7778 | 23.8889 | 23.8889 | 46.1111 |  |  | From PNNL Prototype Buildings HotelSmall, Warehouse
PSZ-AC DX Unitary Package EIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.29714 | 0.043093 | -0.00074877 | 0.0059773 | 0.00048211 | -0.00095645 |  |  |  |  | 12.7778 | 23.8889 | 21.1111 | 46.1111 |  |  | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall,SchoolPrimary
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_CapFT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.42415 | 0.04426 | -0.00042 | 0.00333 | -8e-05 | -0.00021 |  |  |  |  | 17 | 22 | 29 | 46 |  |  | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
PSZ-AC_CoolCLennoxStandard10Ton_TGA120S2B_PLR | DX Cooling Coil | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.771; coeff_2: 0.229; coeff_3: 0 | 0 | 1 |  |  |  |  | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
PSZ-AC_CoolCStandard10Ton_EIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 1.2365 | -0.02431 | 0.00057 | -0.01434 | 0.00063 | -0.00038 |  |  |  |  | 17 | 22 | 29 | 46 |  |  | From PNNL Prototype Buildings OutPatientHealtCare, RestaurantFastFood, RestaurantSitDown, SchoolPrimary, SchoolSecondary
PSZ-AC_Unitary_PackagecoolCapFT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.76696 | 0.010776 | -4.147e-05 | 0.0013496 | -0.00026114 | 0.00045749 |  |  |  |  | 12.7778 | 23.8889 | 21.1111 | 46.1111 |  |  | From PNNL Prototype Buildings RetailStandalone, RetailStripMall, SchoolPrimary
PSZ-AC_Unitary_PackagecoolEIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.156; coeff_2: -0.1816; coeff_3: 0.0256 | 0.5 | 1.5
PSZ-AC_Unitary_PackagecoolFFF | DX Cooling Coil | Quadratic | QRatio | FlowRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0 | 0.5 | 1.5
PSZ-AC_Unitary_PackagecoolPLR | DX Cooling Coil | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.75; coeff_2: 0.25; coeff_3: 0 | 0 | 1 |  |  |  |  | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
PSZ-AC:1_Unitary_PackagecoolEIRFFF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.156; coeff_2: -0.1816; coeff_3: 0.0256 | 0.5 | 1.5 |  |  |  |  | From PNNL Prototype Buildings RetailStandAlone, RetailStripMall, SchoolPrimary
PSZ-Fine Storage DX Coil Cap-FT | DX Cooling Coil | BiQuadratic | QRatio | Twb | Toadb | 0.94259 | 0.0095433 | 0.00068377 | -0.011043 | 5.249e-06 | -9.72e-06 |  |  |  |  | 12.7778 | 23.8889 | 23.8889 | 46.1111 |  |  | From PNNL Prototype Buildings HotelSmall, Warehouse
PSZ-Fine Storage Heating Coil PLF-FPLR | DX Heating Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0; coeff_4: 0 | 0 | 1 |  |  |  |  | From Prototype Buildings
PSZ-Office Heating Coil PLF-FPLR | DX Heating Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0; coeff_4: 0 | 0 | 1 |  |  |  |  | From Prototype Buildings
PSZ135to240_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
PSZ135to240_BF_fT | BF_fT | BiQuadratic |  | T | T | 43.2696 | -4.8983 | 0.14839 | 0.094738 | 0.0021319 | -0.013414 | [8 empty] | 0 | 4.04 | From .dat files included with MASControl2
PSZ135to240_CEIR_fPLR | CEIR_fPLR | Cubic | EIRRatio | PLR |  | coeff_1: 0.0184; coeff_2: 1.15; coeff_3: -0.208; coeff_4: 0.0423 | [6 empty] | From .dat files included with MASControl2
PSZ135to240_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.6277 | -0.060192 | 0.0026017 | -0.0056537 | 2.66e-05 | -0.00040824 | [10 empty] | From .dat files included with MASControl2
PSZ135to240_CLoss_fPLR | CLoss_fPLR | Cubic |  | PLR |  | coeff_1: 0.852; coeff_2: 0.203; coeff_3: -0.0423; coeff_4: 0.00938 |  |  |  |  | 0.8024 | 1.0728 | From .dat files included with MASControl2
PSZ135to240_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 0.40187 | 0.19204 | -0.0077436 | -0.019568 | -4.15e-05 | 0.00077436 | [10 empty] | From .dat files included with MASControl2
PSZ135to240_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | -0.044906 | 0.070595 | -0.0021643 | 0.0044086 | 0.00041148 | -0.00024592 | [10 empty] | From .dat files included with MASControl2
PSZ135to240_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PSZ135to240_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PSZ240to760_BF_fFlow | BF_fFlow | Linear | QRatio | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
PSZ240to760_BF_fT | BF_fT | BiQuadratic |  | T | T | 15.8725 | -1.6605 | 0.041148 | 0.03014 | 0.00027896 | 0.00047628 | [8 empty] | 0 | 3.252 | From .dat files included with MASControl2
PSZ240to760_CEIR_fPLR | CEIR_fPLR | Cubic | EIRRatio | PLR |  | coeff_1: 2.63; coeff_2: -9.5; coeff_3: 14.3; coeff_4: -6.4 | [6 empty] | From .dat files included with MASControl2
PSZ240to760_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.2791 | -0.02911 | 0.0016718 | -0.0022664 | -3.1e-05 | -0.00033372 | [10 empty] | From .dat files included with MASControl2
PSZ240to760_CLoss_fPLR | CLoss_fPLR | Cubic |  | PLR |  | coeff_1: 0.964; coeff_2: 0.289; coeff_3: 0.183; coeff_4: -0.131 |  |  |  |  | 0.96 | 1.3 | From .dat files included with MASControl2
PSZ240to760_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 2.6408 | -0.061521 | -0.0004698 | -0.010835 | -2.89e-05 | 0.00022291 | [10 empty] | From .dat files included with MASControl2
PSZ240to760_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.33661 | 0.048794 | -0.0011632 | -0.005994 | 0.00067716 | -0.00069012 | [10 empty] | From .dat files included with MASControl2
PSZ240to760_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PSZ240to760_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PSZ65to135_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
PSZ65to135_BF_fT | BF_fT | BiQuadratic |  | T | T | 14.9313 | -1.5725 | 0.04698 | 0.0015984 | 0.00096552 | -0.0031979 | [8 empty] | 0 | 3.509 | From .dat files included with MASControl2
PSZ65to135_CEIR_fPLR | CEIR_fPLR | Cubic | EIRRatio | PLR |  | coeff_1: 0.0184; coeff_2: 1.15; coeff_3: -0.208; coeff_4: 0.0423 | [6 empty] | From .dat files included with MASControl2
PSZ65to135_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.2518 | -0.027667 | 0.0011534 | 0.0035388 | -0.00013414 | -0.00016751 | [10 empty] | From .dat files included with MASControl2
PSZ65to135_CLoss_fPLR | CLoss_fPLR | Cubic |  | PLR |  | coeff_1: 0.882; coeff_2: 0.211; coeff_3: -0.0439; coeff_4: 0.0098 |  |  |  |  | 0.8323 | 1.1087 | From .dat files included with MASControl2
PSZ65to135_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.7733 | 0.038369 | -0.0038556 | -0.010902 | -0.00013835 | 0.00070632 | [10 empty] | From .dat files included with MASControl2
PSZ65to135_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.54311 | 0.03102 | -0.00090072 | -0.014966 | 0.0006966 | -0.00019991 | [10 empty] | From .dat files included with MASControl2
PSZ65to135_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PSZ65to135_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PTAC_EIR_fPLR | PkgdTerminalACS | Cubic | EIRRatio | PLR |  | coeff_1: 0.125; coeff_2: 0.875; coeff_3: 0; coeff_4: 0 | [6 empty] | From .dat files included with MASControl2
PTAC-Bypass-Factor-fAirflow | PkgdTerminalAC | Quadratic | QRatio | Airflow |  | coeff_1: -2.28; coeff_2: 5.21; coeff_3: -1.93 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
PTAC-Bypass-Factor-fEWB&EDB | PkgdTerminalAC | BiQuadratic | QRatio | EWB | EDB | -0.21966 | 0.099461 | 0.00102 | -0.020394 | 0.00036 | -0.0012053 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PTAC-Cool-Cap-fEWB&OAT | PkgdTerminalAC | BiQuadratic | QRatio | EWB | OAT | 0.93865 | 0.0095364 | 0.000684 | -0.011038 | 5.25e-06 | -9.72e-06 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PTAC-EIR-fEWB&OAT | PkgdTerminalAC | BiQuadratic | EIRRatio | EWB | OAT | 0.34209 | 0.034844 | -0.000625 | 0.0049689 | 0.000438 | -0.000728 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PTAC-EIR-fPLR | PkgdTerminalAC | Linear | EIRRatio | PLR |  | coeff_1: 0.125; coeff_2: 0.875 | [6 empty] | From .dat files included with MASControl2
PTAC-Sens-Cap-fAirflow | PkgdTerminalAC | Linear | QRatio | Airflow |  | coeff_1: 0.6; coeff_2: 0.4 | [6 empty] | From .dat files included with MASControl2
PTAC-Sens-Cap-fEWB&OAT | PkgdTerminalAC | BiQuadratic | QRatio | EWB | OAT | 3.2723 | -0.14984 | 0.0014029 | 0.0047124 | -0.000162 | 0.000207 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PTACHPACEIRFT | DX Cooling Coil | BiQuadratic | EIRRatio | Twb | Toadb | 0.34241 | 0.034885 | -0.0006237 | 0.0049772 | 0.00043795 | -0.00072803 |  |  |  |  | 12.7778 | 23.8889 | 18.3 | 46.1111 |  |  | From DOE Reference Buildings SmallHotel
Pump-Head-fFlow | Pumps | Quadratic | QRatio | Flow |  | coeff_1: 1.3535; coeff_2: 33.8; coeff_3: -1660000 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Pump-Power-fFlow | Pumps | Quadratic |  | Flow |  | coeff_1: 0.36977; coeff_2: 1780.6538; coeff_3: -943000 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
PVV240to760_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
PVV240to760_BF_fT | BF_fT | BiQuadratic |  | T | T | 8.7477 | -1.2545 | 0.034992 | 0.21989 | -0.0022129 | -0.002848 | [8 empty] | 0 | 3.2 | From .dat files included with MASControl2
PVV240to760_CEIR_fPLR | CEIR_fPLR | Cubic | EIRRatio | PLR |  | coeff_1: 0.124; coeff_2: 0.376; coeff_3: 1.29; coeff_4: -0.794 | [6 empty] | From .dat files included with MASControl2
PVV240to760_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 0.95212 | -0.010977 | 0.0012312 | -0.00072792 | -4.54e-05 | -0.00017399 | [10 empty] | From .dat files included with MASControl2
PVV240to760_CLoss_fPLR | CLoss_fPLR | Cubic |  | PLR |  | coeff_1: 0; coeff_2: 1; coeff_3: 0; coeff_4: 0 |  |  |  |  | 0.1 | 1 | From .dat files included with MASControl2
PVV240to760_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.9165 | 0.0047736 | -0.002336 | -0.013757 | -3.23e-05 | 0.00057672 | [10 empty] | From .dat files included with MASControl2
PVV240to760_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.38019 | 0.024149 | -0.00047952 | 0.011117 | 0.00052488 | -0.0010238 | [10 empty] | From .dat files included with MASControl2
PVV240to760_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PVV240to760_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 | [10 empty] | From .dat files included with MASControl2
PVVT-Bypass-Factor-fAirflow | PkgdVVVT | Quadratic | QRatio | Airflow |  | coeff_1: -0.254; coeff_2: 1.22; coeff_3: 0.036 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
PVVT-Bypass-Factor-fEWB&EDB | PkgdVVVT | BiQuadratic | QRatio | EWB | EDB | 0.85028 | 0.014257 | 0.000184 | -0.014792 | -5.48e-06 | 0.000487 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PVVT-Cool-Cap-fEWB&OAT | PkgdVVVT | BiQuadratic | QRatio | EWB | OAT | 0.86783 | 0.014239 | 0.000554 | -0.0075581 | 3.3e-05 | -0.000192 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PVVT-Cool-EIR-fEWB&OAT | PkgdVVVT | BiQuadratic | EIRRatio | EWB | OAT | 0.121 | 0.028534 | -0.000411 | 0.021349 | 0.000161 | -0.00068 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
PVVT-Cool-EIR-fPLR | PkgdVVVT | Cubic | EIRRatio | PLR |  | coeff_1: 0.201; coeff_2: -0.0312; coeff_3: 1.9505; coeff_4: -1.1205 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
PVVT-Heat-Cap-fEDB&OAT | PkgdVVVT | BiQuadratic | QRatio | EDB | OAT | 0.74201 | 0 | 0 | 0.030669 | 3.23e-05 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
PVVT-Heat-EIR-fEDB&OAT | PkgdVVVT | BiQuadratic | EIRRatio | EDB | OAT | 1.2557 | 0 | 0 | -0.039953 | 0.0010886 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
PVVT-Heat-EIR-fPLR | PkgdVVVT | Cubic | EIRRatio | PLR |  | coeff_1: 0.0857; coeff_2: 0.939; coeff_3: -0.183; coeff_4: 0.159 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
PVVT-Sens-Cap-fEWB&OAT | PkgdVVVT | BiQuadratic | QRatio | EWB | OAT | 2.9323 | -0.09446 | 0.0002 | -0.0071738 | 1.03e-05 | 0.000109 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T1-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.63562; coeff_2: 0.0035335; coeff_3: 0.000161 |  |  |  |  | 0.7533 | 1.2802 | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T1-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 1.1135; coeff_2: -0.030899; coeff_3: 0.000739 |  |  |  |  | 0.95008 | 1.6068 | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T2-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.58083; coeff_2: 0.0049484; coeff_3: 0.000161 |  |  |  |  | 0.7262 | 1.3046 | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T2-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.97016; coeff_2: -0.02268; coeff_3: 0.000625 |  |  |  |  | 0.94391 | 1.5654 | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T3-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.3588; coeff_2: 0.00732; coeff_3: 0.000257 |  |  |  |  | 0.5728 | 1.4917 | From .dat files included with MASControl2
Rcmp-kW-f-Tc-T3-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.65654; coeff_2: -0.0039924; coeff_3: 0.00035 |  |  |  |  | 0.94199 | 1.4181 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T1-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.90448; coeff_2: -0.0089722; coeff_3: 0.000303 |  |  |  |  | 0.8518 | 1.2802 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T1-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 1.1135; coeff_2: -0.030899; coeff_3: 0.000739 |  |  |  |  | 0.95008 | 1.6068 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T2-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.88733; coeff_2: -0.0095165; coeff_3: 0.000328 |  |  |  |  | 0.8326 | 1.3046 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T2-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.97016; coeff_2: -0.02268; coeff_3: 0.000625 |  |  |  |  | 0.94391 | 1.5654 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T3-Hi-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.82959; coeff_2: -0.014866; coeff_3: 0.000512 |  |  |  |  | 0.7434 | 1.4917 | From .dat files included with MASControl2
Rcmp-kW2-f-Tc-T3-Low-Eff | Refrigeration | Quadratic |  | Tc |  | coeff_1: 0.65654; coeff_2: -0.0039924; coeff_3: 0.00035 |  |  |  |  | 0.94199 | 1.4181 | From .dat files included with MASControl2
Rcond-Fan-Pwr-fPLR-ACpress | Refrigeration | Linear |  | PLR |  | coeff_1: 0; coeff_2: 1 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
Rcond-Fan-Pwr-fPLR-Damper | Refrigeration | Linear |  | PLR |  | coeff_1: 0.3; coeff_2: 0.7 |  |  |  |  | 0.3 | 1 | From .dat files included with MASControl2
RecipAir-Cap-fCHWT&DBT | HermReciprocatg | BiQuadratic | QRatio | CHWT | DBT | 1.1067 | 0.040198 | 0.000286 | -0.0095529 | 5.22e-06 | -0.000255 | [10 empty] | From .dat files included with MASControl2
RecipAir-EIR-fCHWT&DBT | HermReciprocatg | BiQuadratic | EIRRatio | CHWT | DBT | 0.53866 | -0.0081422 | 0.000125 | 0.011091 | 0.000164 | -0.000342 | [10 empty] | From .dat files included with MASControl2
RecipAir-EIR-fPLR-1Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | 0.038926 | 1.0753 | -0.10724 | -0.0010507 | 9.43e-06 | 0.00053635 | [10 empty] | From .dat files included with MASControl2
RecipAir-EIR-fPLR-2Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | 0.048122 | 0.69573 | 0.23494 | 0.00081938 | -3.86e-06 | 3.79e-05 | [10 empty] | From .dat files included with MASControl2
RecipAir-EIR-fPLR-3Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | 0.032967 | 0.57721 | 0.33923 | 0.0027864 | -3.11e-05 | -0.000119 | [10 empty] | From .dat files included with MASControl2
RecipAir-EIR-fPLR-4Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | 0.0043488 | 0.61917 | 0.32643 | 0.0032234 | -3.33e-05 | -0.00051421 | [10 empty] | From .dat files included with MASControl2
RecipH2O-Cap-fCHWT&ECT | HermReciprocatg | BiQuadratic | QRatio | CHWT | ECT | 1.069 | 0.036781 | 0.000334 | -0.010426 | 2.17e-05 | -0.000208 | [10 empty] | From .dat files included with MASControl2
RecipH2O-EIR-fCHWT&ECT | HermReciprocatg | BiQuadratic | EIRRatio | CHWT | ECT | 0.51329 | -0.015039 | 0.000362 | 0.015399 | 0.000228 | -0.000409 | [10 empty] | From .dat files included with MASControl2
RecipH2O-EIR-fPLR&dT-1Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | -0.014297 | 0.95361 | 0.018053 | 0.002823 | -1.99e-05 | -0.00049799 | [10 empty] | From .dat files included with MASControl2
RecipH2O-EIR-fPLR&dT-2Comp/Ckt | HermReciprocatg | BiQuadratic | EIRRatio | PLR | dT | 0.023918 | 0.88947 | 0.077931 | -0.00047443 | 2.33e-05 | 0.000324 | [10 empty] | From .dat files included with MASControl2
RecipRemote-Cap-fCHWT&SCT | HermReciprocatg | BiQuadratic | QRatio | CHWT | SCT | 1.2798 | 0.051393 | 0.000332 | -0.0095228 | -1.97e-05 | -0.000269 | [10 empty] | From .dat files included with MASControl2
RecipRemote-EIR-fCHWT&SCT | HermReciprocatg | BiQuadratic | EIRRatio | CHWT | SCT | 0.25315 | -0.015359 | 0.000506 | 0.0097177 | 0.000171 | -0.000382 | [10 empty] | From .dat files included with MASControl2
RecipRemote-EIR-fPLR-1Comp/Ckt | HermReciprocatg | Quadratic | EIRRatio | PLR |  | coeff_1: 0.035211; coeff_2: 0.93266; coeff_3: 0.032128 | [6 empty] | From .dat files included with MASControl2
RecipRemote-EIR-fPLR-2Comp/Ckt | HermReciprocatg | Quadratic | EIRRatio | PLR |  | coeff_1: 0.02511; coeff_2: 0.89341; coeff_3: 0.081475 | [6 empty] | From .dat files included with MASControl2
Refg-Condenser-Cap-fCondT&WBT | Refrigeration | BiQuadratic | QRatio | CondT | WBT | 0.15373 | 0.0094281 | 0.000693 | -0.020963 | -0.000702 | 0.000302 | [8 empty] | 0.2 | 2.222 | From .dat files included with MASControl2
Refg-kW-fECT-T1 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 0.75342; coeff_2: -0.021215; coeff_3: 0.000739 |  |  |  |  | 0.85036 | 1.7473 | From .dat files included with MASControl2
Refg-kW-fECT-T2 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 1.0032; coeff_2: -0.029057; coeff_3: 0.000765 |  |  |  |  | 0.85903 | 1.593 | From .dat files included with MASControl2
Refg-kW-fECT-T3 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 0.67162; coeff_2: -0.0074358; coeff_3: 0.000424 |  |  |  |  | 0.87308 | 1.4669 | From .dat files included with MASControl2
Refg-kW-fPLR | Refrigeration | Quadratic |  | PLR |  | coeff_1: 0.0383; coeff_2: 1.08; coeff_3: -0.11613 |  |  |  |  | 0.1 | 1.2 | From .dat files included with MASControl2
Refg-kW2-fECT-T1 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 0.75342; coeff_2: -0.021215; coeff_3: 0.000739 |  |  |  |  | 0.85036 | 1.7473 | From .dat files included with MASControl2
Refg-kW2-fECT-T2 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 1.0032; coeff_2: -0.029057; coeff_3: 0.000765 |  |  |  |  | 0.85903 | 1.593 | From .dat files included with MASControl2
Refg-kW2-fECT-T3 | Refrigeration | Quadratic |  | ECT |  | coeff_1: 0.67162; coeff_2: -0.0074358; coeff_3: 0.000424 |  |  |  |  | 0.87308 | 1.4669 | From .dat files included with MASControl2
Residential Fix Vol-Fan EIR | FanEIR-FPLR | Linear | EIRRatio | PLR |  | coeff_1: 1; coeff_2: 0 | [6 empty] | From .dat files included with MASControl2
Residential Var Vol-Fan EIR | FanEIR-FPLR | Cubic | EIRRatio | PLR |  | coeff_1: 0.000281; coeff_2: -0.0579; coeff_3: 0.586; coeff_4: 0.471 | [6 empty] | From .dat files included with MASControl2
RestaurantFastFood Kitchen_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.0236; coeff_2: 0.0006; coeff_3: 0; coeff_4: 0 | -35 | 20 |  |  |  |  | From Prototype Buildings
RestaurantFastFood Kitchen_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: 6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20 |  |  |  |  | From Prototype Buildings
RESVVT-Bypass-Factor-fAirflow | ResidentialVVVT | Quadratic | QRatio | Airflow |  | coeff_1: -0.254; coeff_2: 1.22; coeff_3: 0.036 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
RESVVT-Bypass-Factor-fEWB&EDB | ResidentialVVVT | BiQuadratic | QRatio | EWB | EDB | 0.85086 | 0.014257 | 0.000184 | -0.014759 | -5.48e-06 | 0.000487 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-Cap-fEWB&OAT | ResidentialVVVT | BiQuadratic | QRatio | EWB | OAT | 0.47523 | 0.040064 | 0.000226 | -0.00084715 | -7.32e-06 | -0.000447 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-Cap-fRPM&OAT | ResidentialVVVT | BiQuadratic | QRatio | RPM | OAT | -686.394 | -427.2546 | -66.3856 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-CondFan-fPLR&OAT | ResidentialVVVT | BiQuadratic |  | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-CycleLoss-fPLR | ResidentialVVVT | Linear | QRatio | PLR |  | coeff_1: 0.7; coeff_2: 0.3 | [6 empty] | From .dat files included with MASControl2
RESVVT-Cool-EIR-fEWB&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | EWB | OAT | 0.63154 | -0.012168 | 0.000509 | 0.015536 | 0.000273 | -0.000679 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-EIR-fPLR | ResidentialVVVT | Linear | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1 | [6 empty] | From .dat files included with MASControl2
RESVVT-Cool-EIR-fRPM&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | RPM | OAT | 35.1027 | 10.5042 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-EIR-LoSpeed-fEWB&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | EWB | OAT | 0.77672 | -0.034271 | 0.000784 | 0.01466 | 0.000489 | -0.000752 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-Waste-Heat-fEWB&OAT | ResidentialVVVT | BiLinear | QRatio | EWB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Cool-Waste-Heat-fRPM&OAT | ResidentialVVVT | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
RESVVT-Heat-Cap-fEDB&OAT | ResidentialVVVT | BiQuadratic | QRatio | EDB | OAT | 0.7716 | 0 | 0 | 0.02754 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-Cap-fRPM&OAT | ResidentialVVVT | BiQuadratic | QRatio | RPM | OAT | -483.189 | -303.9732 | -47.6919 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-CondFan-fPLR&OAT | ResidentialVVVT | BiQuadratic |  | PLR | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-CycleLoss-fPLR | ResidentialVVVT | Linear | QRatio | PLR |  | coeff_1: 0.75; coeff_2: 0.25 | [6 empty] | From .dat files included with MASControl2
RESVVT-Heat-EIR-fEDB&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | EDB | OAT | 1.1544 | 0 | 0 | -0.02448 | 0.000729 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-EIR-fPLR | ResidentialVVVT | Linear | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1 | [6 empty] | From .dat files included with MASControl2
RESVVT-Heat-EIR-fRPM&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | RPM | OAT | 31.9068 | 9.5206 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-EIR-LoSpeed-fEDB&OAT | ResidentialVVVT | BiQuadratic | EIRRatio | EDB | OAT | 1.2544 | 0 | 0 | -0.040685 | 0.0012098 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-Waste-Heat-fEDB&OAT | ResidentialVVVT | BiLinear | QRatio | EDB | OAT | coeff_1: 1; coeff_2: 0; coeff_3: 0 | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Heat-Waste-Heat-fRPM&OAT | ResidentialVVVT | BiQuadratic | QRatio | RPM | OAT | 1 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0 | 1.05 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESVVT-Sens-Cap-fEWB&OAT | ResidentialVVVT | BiLinear | QRatio | EWB | OAT | coeff_1: 2.7867; coeff_2: -0.08208; coeff_3: -0.005292 | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESYS-Bypass-Factor-fAirflow | Residential#1 | Quadratic | QRatio | Airflow |  | coeff_1: -3.01; coeff_2: 6.59; coeff_3: -2.57 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
RESYS-Bypass-Factor-fEWB&EDB | Residential#1 | BiQuadratic | QRatio | EWB | EDB | -1.1641 | 0.20453 | -0.000603 | -0.030361 | 0.00036 | -0.0014648 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESYS-Bypass-Factor-fPLR | ResidentialVVVT | Linear | QRatio | PLR |  | coeff_1: 1; coeff_2: 0 | [6 empty] | From .dat files included with MASControl2
RESYS-Cool-Cap-fEWB&OAT | Residential#1 | BiQuadratic | QRatio | EWB | OAT | 0.7665 | 0.010769 | -4.15e-05 | 0.0013385 | -0.000261 | 0.000457 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESYS-Cool-EIR-fEWB&OAT | Residential#1 | BiQuadratic | EIRRatio | EWB | OAT | 0.29771 | 0.043145 | -0.000748 | 0.0059727 | 0.000482 | -0.000956 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
RESYS-Cool-EIR-fPLR |  | Cubic | EIRRatio | PLR |  | coeff_1: 6.26e-05; coeff_2: 1.18; coeff_3: -0.202; coeff_4: 0.026334 | [6 empty] | From .dat files included with MASControl2
RESYS-Heat-Cap-fEDB&OAT | Residential#1 | BiQuadratic | QRatio | EDB | OAT | 0.75161 | 0 | 0 | 0.027991 | 0.00019 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESYS-Heat-EIR-fEDB&OAT | Residential#1 | BiQuadratic | EIRRatio | EDB | OAT | 1.2311 | 0 | 0 | -0.033494 | 0.000739 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.3333 | 29.4444 |  |  | From .dat files included with MASControl2
RESYS-Heat-EIR-fPLR | Residential#1 | Cubic | EIRRatio | PLR |  | coeff_1: 0.0857; coeff_2: 0.939; coeff_3: -0.18344; coeff_4: 0.15897 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
RESYS-Sens-Cap-fAirflow | Residential#1 | Linear | QRatio | Airflow |  | coeff_1: 0.6; coeff_2: 0.4 | [6 empty] | From .dat files included with MASControl2
RESYS-Sens-Cap-fEWB&OAT | Residential#1 | BiQuadratic | QRatio | EWB | OAT | 3.3128 | -0.16176 | 0.0018436 | 0.010276 | -0.000156 | -2.84e-05 |  |  |  |  | 12.7778 | 29.4444 | 21.1111 | 46.1111 |  |  | From .dat files included with MASControl2
SAC Heating Coil PLF-FPLR | DX Heating Coil | Cubic | EIRRatio | QRatio |  | coeff_1: 0.8; coeff_2: 0.2; coeff_3: 0; coeff_4: 0 | 0 | 1 |  |  |  |  | From Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:1_WALKINFREEZERSingleShelfHorizontal_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.0236; coeff_2: 0.0006; coeff_3: 0; coeff_4: 0 | -35 | 20 |  |  |  |  | From Prototype Buildings
SchoolPrimary Kitchen_ZN_1_FLR_1_Case:2_SELFCONTAINEDDISPLAYCASEMultiShelfVertical_LatentEnergyMult | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: 6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20 |  |  |  |  | From Prototype Buildings
ScrewAir-Cap-fCHWT&DBT | Screw | BiQuadratic | QRatio | CHWT | DBT | 0.97879 | 0.023872 | 0.000587 | -4.78e-05 | -0.000112 | -0.00011 | [10 empty] | From .dat files included with MASControl2
ScrewAir-EIR-fCHWT&DBT | Screw | BiQuadratic | EIRRatio | CHWT | DBT | 0.67297 | -0.00573 | 0.000702 | -0.001196 | 0.00044 | -0.000699 | [10 empty] | From .dat files included with MASControl2
ScrewAir-EIR-fPLR&dT-1Comp/Ckt | Screw | BiQuadratic | EIRRatio | PLR | dT | 0.010407 | 1.0518 | -0.094625 | 0.0029438 | -2.52e-05 | -0.0010858 | [10 empty] | From .dat files included with MASControl2
ScrewAir-EIR-fPLR&dT-2Comp/Ckt | Screw | BiQuadratic | EIRRatio | PLR | dT | 0.09611 | 0.72899 | 0.19517 | -0.00072907 | 6.67e-06 | -0.000175 | [10 empty] | From .dat files included with MASControl2
ScrewH2O-Cap-fCHWT&ECT | Screw | BiQuadratic | QRatio | CHWT | ECT | 1.071 | 0.026935 | 0.000768 | -0.006433 | -9.49e-05 | -6.59e-05 | [10 empty] | From .dat files included with MASControl2
ScrewH2O-EIR-fCHWT&ECT | Screw | BiQuadratic | EIRRatio | CHWT | ECT | 0.5985 | -0.0012335 | 0.000563 | 0.0016027 | 0.000636 | -0.0010941 | [10 empty] | From .dat files included with MASControl2
ScrewH2O-EIR-fPLR&dT-1Comp/Ckt | Screw | BiQuadratic | EIRRatio | PLR | dT | -0.11699 | 1.2635 | -0.21947 | 0.0053016 | 5.47e-05 | -0.0033465 | [10 empty] | From .dat files included with MASControl2
ScrewH2O-EIR-fPLR&dT-2Comp/Ckt | Screw | BiQuadratic | EIRRatio | PLR | dT | -0.27111 | 1.4901 | -0.33198 | 0.017556 | -0.000191 | -0.0082472 | [10 empty] | From .dat files included with MASControl2
ScrewRemote-Cap-fCHWT&SCT | Screw | BiQuadratic | QRatio | CHWT | SCT | 1.1641 | 0.04837 | 0.000493 | -0.0024282 | -0.000109 | -0.000269 | [10 empty] | From .dat files included with MASControl2
ScrewRemote-EIR-fCHWT&SCT | Screw | BiQuadratic | EIRRatio | CHWT | SCT | 0.79518 | -0.0091015 | 0.0017078 | -0.015353 | 0.000488 | -0.000932 | [10 empty] | From .dat files included with MASControl2
ScrewRemote-EIR-fPLR-1Comp/Ckt | Screw | Quadratic | EIRRatio | PLR |  | coeff_1: 0.07043; coeff_2: 1.0168; coeff_3: -0.087262 | [6 empty] | From .dat files included with MASControl2
ScrewRemote-EIR-fPLR-2Comp/Ckt | Screw | Quadratic | EIRRatio | PLR |  | coeff_1: 0.081382; coeff_2: 0.72725; coeff_3: 0.19137 | [6 empty] | From .dat files included with MASControl2
ScrollChlrAirCoolCap-fCHW&OAT | Chiller | BiQuadratic | QRatio | CHWT | OAT | 1.0523 | 0.033561 | 0.000215 | -0.0051808 | -4.42e-05 | -0.000215 | [10 empty] | From .dat files included with MASControl2
ScrollChlrAirCoolEIR-fCHW&OAT | Chiller | BiQuadratic | EIRRatio | CHWT | OAT | 0.58334 | -0.0040362 | 0.000468 | -0.00022448 | 0.000481 | -0.000682 | [10 empty] | From .dat files included with MASControl2
ScrollChlrAirCoolEIR-fPLR | Chiller | Quadratic | EIRRatio | PLR |  | coeff_1: 0.033666; coeff_2: 0.53153; coeff_3: 0.43481 | [6 empty] | From .dat files included with MASControl2
Si-Film_Spectral-fAirMass | PV-Module | Cubic |  | AirMass |  | coeff_1: 0.95692; coeff_2: 0.040797; coeff_3: -0.0086938; coeff_4: 0.00042887 | [6 empty] | From .dat files included with MASControl2
Single Shelf Horizontal Latent Energy Multiplier_After2004 | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.0236; coeff_2: 0.0006; coeff_3: 0; coeff_4: 0 | -35 | 20 |  |  |  |  | From Reference Buildings
Single Shelf Horizontal Latent Energy Multiplier_Pre2004 | Refrigerated Case | Cubic |  |  |  | coeff_1: 0.020376; coeff_2: 0.00024378; coeff_3: 1.14e-05; coeff_4: 1.811e-07 | -35 | 20 |  |  |  |  | From Reference Buildings
Single zone VAV fan | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.027828; coeff_2: 0.026583; coeff_3: -0.087069; coeff_4: 1.0309 | 0 | 1 |  |  | 0.1 |  | Baseline for System Type 11 from ANSI/ASHRAE/IES Standard 90.1-2016 - Energy Standard for Buildings Except Low-Rise Residential Performance Rating Method
Small-CHW-Bypass-fAirflow | CHWCoils | Quadratic | QRatio | Airflow |  | coeff_1: -0.718; coeff_2: 1.91; coeff_3: -0.189 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Small-CHW-Coil-Bypass-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | 1.0966 | 0.001908 | 0.000369 | -0.005647 | 2.46e-05 | -0.000277 |  |  |  |  | 15.5556 | 29.4444 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Small-CHW-Coil-Cap-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | -0.28205 | -0.022212 | 0.0054432 | 0.029722 | 0.000804 | -0.0033372 |  |  |  |  | 15.5556 | 29.4444 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Small-CHW-Sens-Cap-fAirflow | CHWCoils | Quadratic | QRatio | Airflow |  | coeff_1: 0.155; coeff_2: 1.01; coeff_3: -0.16 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Small-CHW-Sens-Cap-fEWB&EDB | CHWCoils | BiQuadratic | QRatio | EWB | EDB | -0.41515 | -0.040558 | 0.0014062 | 0.086508 | 0.000444 | -0.0018436 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 29.4444 |  |  | From .dat files included with MASControl2
Smooth_Optical-fAOI | PV-Module | Cubic |  | AOI |  | coeff_1: 3.7625; coeff_2: -0.15947; coeff_3: 0.0030219; coeff_4: -1.91e-05 | [6 empty] | From .dat files included with MASControl2
Split DX Coil EIR-FF | DX Cooling Coil | Quadratic | EIRRatio | FlowRatio |  | coeff_1: 1.1552; coeff_2: -0.1808; coeff_3: 0.0256 | 0.5 | 1.5 |  |  |  |  | From PNNL Prototype Buildings ApartmentMidRise, HotelSmall, Warehouse
SpltAC1Sp_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltAC1Sp_BF_fT | BF_fT | BiQuadratic |  | T | T | 8.5136 | -0.63007 | 0.016589 | -0.045014 | 0.0010789 | -0.0018954 | [8 empty] | 0 | 3.33 | From .dat files included with MASControl2
SpltAC1Sp_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 7e-05; coeff_2: 1.23; coeff_3: -0.307; coeff_4: 0.0756 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 0.00012; coeff_2: 1.2; coeff_3: -0.261; coeff_4: 0.0596 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -7e-05; coeff_2: 1.17; coeff_3: -0.213; coeff_4: 0.0438 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 0.67916 | 0.016938 | 0.00069336 | 0.0045576 | -8.42e-05 | -0.00047628 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.805; coeff_2: 0.233; coeff_3: -0.038 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.827; coeff_2: 0.203; coeff_3: -0.03 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.852; coeff_2: 0.17; coeff_3: -0.0219 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 2.7312 | -0.10297 | 0.00093636 | 0.0047786 | -9.07e-05 | -0.00020282 | [10 empty] | From .dat files included with MASControl2
SpltAC1Sp_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.73905 | -0.0077897 | 0.0001283 | -0.00027 | 0.0006642 | -0.000648 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-ge45_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltAC1Sp-ge45_BF_fT | BF_fT | BiQuadratic |  | T | T | 16.9001 | -1.7476 | 0.050544 | 0.14289 | 0.00048924 | -0.0090396 | [8 empty] | 0 | 3.76 | From .dat files included with MASControl2
SpltAC1Sp-ge45_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1.18; coeff_3: -0.223; coeff_4: 0.0468 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 8e-05; coeff_2: 1.15; coeff_3: -0.183; coeff_4: 0.0343 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -0.0001; coeff_2: 1.12; coeff_3: -0.14; coeff_4: 0.0225 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.2403 | -0.034675 | 0.001876 | 0.0010685 | -5.7e-05 | -0.0003564 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-ge45_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.847; coeff_2: 0.177; coeff_3: -0.0235 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.869; coeff_2: 0.149; coeff_3: -0.0172 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.893; coeff_2: 0.118; coeff_3: -0.0112 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.8261 | 0.019994 | -0.0028415 | -0.014226 | -5.77e-05 | 0.00064152 | [10 empty] | From .dat files included with MASControl2
SpltAC1Sp-ge45_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.093776 | 0.067478 | -0.0019213 | -0.0031176 | 0.00067068 | -0.0005832 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-ge45_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-ge45_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-lt45_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltAC1Sp-lt45_BF_fT | BF_fT | BiQuadratic |  | T | T | 22.9322 | -2.2916 | 0.063504 | 0.080071 | 0.00076464 | -0.0068364 | [8 empty] | 0 | 3.3 | From .dat files included with MASControl2
SpltAC1Sp-lt45_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1.18; coeff_3: -0.223; coeff_4: 0.0468 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 8e-05; coeff_2: 1.15; coeff_3: -0.183; coeff_4: 0.0343 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -0.0001; coeff_2: 1.12; coeff_3: -0.14; coeff_4: 0.0225 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.13 | -0.022234 | 0.0015228 | -3.53e-05 | -4.34e-05 | -0.00032724 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-lt45_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.847; coeff_2: 0.177; coeff_3: -0.0235 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.869; coeff_2: 0.149; coeff_3: -0.0172 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.893; coeff_2: 0.118; coeff_3: -0.0112 | [6 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.4985 | 0.047851 | -0.0034992 | -0.01085 | -5.48e-05 | 0.00047628 | [10 empty] | From .dat files included with MASControl2
SpltAC1Sp-lt45_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.09712 | 0.053626 | -0.0014483 | 0.0040644 | 0.00062208 | -0.000729 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-lt45_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC1Sp-lt45_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpHiSEER_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1.75; coeff_2: -1578.5656 |  |  |  |  | 1 | 1.189 | From .dat files included with MASControl2
SpltAC2SpHiSEER_BF_fT | BF_fT | BiQuadratic |  | T | T | 20.0302 | -1.9228 | 0.051516 | 0.086184 | 0.0011502 | -0.0076788 | [8 empty] | 0 | 3.92 | From .dat files included with MASControl2
SpltAC2SpHiSEER_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 0.00635; coeff_2: 1.12; coeff_3: -0.139; coeff_4: 0.016 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: -0.00144; coeff_2: 1.12; coeff_3: -0.14; coeff_4: 0.022 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -0.00726; coeff_2: 1.11; coeff_3: -0.132; coeff_4: 0.0262 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.524 | -0.066593 | 0.0029938 | 0.0016229 | -6.51e-05 | -0.00048924 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpHiSEER_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.923; coeff_2: 0.153; coeff_3: -0.0156 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.94; coeff_2: 0.124; coeff_3: -0.0109 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.959; coeff_2: 0.0934; coeff_3: -0.00688 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.54 | 0.038275 | -0.0029776 | -0.011491 | -0.00010044 | 0.0005346 | [10 empty] | From .dat files included with MASControl2
SpltAC2SpHiSEER_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | -0.17251 | 0.11766 | -0.00324 | -0.01152 | 0.00077112 | -0.00057024 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpHiSEER_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpHiSEER_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpLoSEER_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1.75; coeff_2: -1578.5656 |  |  |  |  | 1 | 1.189 | From .dat files included with MASControl2
SpltAC2SpLoSEER_BF_fT | BF_fT | BiQuadratic |  | T | T | 10.8204 | -1.0413 | 0.025499 | 0.22906 | 0.00062856 | -0.011761 | [8 empty] | 0 | 5.76 | From .dat files included with MASControl2
SpltAC2SpLoSEER_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: -0.00016; coeff_2: 1.12; coeff_3: -0.143; coeff_4: 0.0206 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: -0.00146; coeff_2: 1.1; coeff_3: -0.119; coeff_4: 0.0176 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: 0.00284; coeff_2: 1.06; coeff_3: -0.0687; coeff_4: 0.00523 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.5489 | -0.064807 | 0.0031007 | -0.00042538 | -2.55e-05 | -0.00060264 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpLoSEER_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.856; coeff_2: 0.121; coeff_3: -0.0124 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.872; coeff_2: 0.0941; coeff_3: -0.00752 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.889; coeff_2: 0.0695; coeff_3: -0.00646 | [6 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 2.322 | -0.028696 | -0.0012409 | -0.020124 | -4.05e-05 | 0.0006804 | [10 empty] | From .dat files included with MASControl2
SpltAC2SpLoSEER_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | -0.28138 | 0.13431 | -0.0036936 | -0.017374 | 0.00096552 | -0.00075168 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpLoSEER_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltAC2SpLoSEER_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltACEvap_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltACEvap_BF_fT | BF_fT | BiQuadratic |  | T | T | 16.06 | -1.566 | 0.0405 | 1.75e-10 | 3.24e-12 | 3.24e-12 | [8 empty] | 0 | 3.97 | From .dat files included with MASControl2
SpltACEvap_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1; coeff_3: 0; coeff_4: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1; coeff_3: 0; coeff_4: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: 0; coeff_2: 1; coeff_3: 0; coeff_4: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 0.63021 | 0.017158 | 0.00069012 | -0.0037469 | 0.00021254 | -0.0005508 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltACEvap_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.94; coeff_2: 0.06; coeff_3: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.97; coeff_2: 0.03; coeff_3: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 1; coeff_2: 0; coeff_3: 0 | [6 empty] | From .dat files included with MASControl2
SpltACEvap_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.9516 | -0.015401 | -0.0012798 | -0.0011009 | 0.00019472 | -0.00054432 | [10 empty] | From .dat files included with MASControl2
SpltACEvap_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 1.2072 | -0.052855 | 0.00053136 | 0.026129 | -0.00045684 | 0.0005508 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltACEvap_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltACEvap_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpCom_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltHP1SpCom_BF_fT | BF_fT | BiQuadratic |  | T | T | 8.5136 | -0.63007 | 0.016589 | -0.045014 | 0.0010789 | -0.0018954 | [8 empty] | 0 | 3.33 | From .dat files included with MASControl2
SpltHP1SpCom_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 7e-05; coeff_2: 1.23; coeff_3: -0.307; coeff_4: 0.0756 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 0.00012; coeff_2: 1.2; coeff_3: -0.261; coeff_4: 0.0596 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -7e-05; coeff_2: 1.17; coeff_3: -0.213; coeff_4: 0.0438 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 0.67916 | 0.016938 | 0.00069336 | 0.0045576 | -8.42e-05 | -0.00047628 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpCom_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.805; coeff_2: 0.233; coeff_3: -0.038 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.827; coeff_2: 0.203; coeff_3: -0.03 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.852; coeff_2: 0.17; coeff_3: -0.0219 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpCom_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 2.7312 | -0.10297 | 0.00093636 | 0.0047786 | -9.07e-05 | -0.00020282 | [10 empty] | From .dat files included with MASControl2
SpltHP1SpCom_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.73905 | -0.0077897 | 0.0001283 | -0.00027 | 0.0006642 | -0.000648 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpCom_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0.8187 | 0.01407 | 0.00011794 | -0.015791 | 0.00022226 | -0.00030002 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpCom_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0.85517 | -0.0036314 | -6.19e-06 | 0.026447 | 0.00041148 | -0.00014126 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpRes_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1; coeff_2: 0 |  |  |  |  | 0 | 1 | From .dat files included with MASControl2
SpltHP1SpRes_BF_fT | BF_fT | BiQuadratic |  | T | T | 8.5136 | -0.63007 | 0.016589 | -0.045014 | 0.0010789 | -0.0018954 | [8 empty] | 0 | 3.33 | From .dat files included with MASControl2
SpltHP1SpRes_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 7e-05; coeff_2: 1.23; coeff_3: -0.307; coeff_4: 0.0756 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: 0.00012; coeff_2: 1.2; coeff_3: -0.261; coeff_4: 0.0596 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -7e-05; coeff_2: 1.17; coeff_3: -0.213; coeff_4: 0.0438 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 0.67916 | 0.016938 | 0.00069336 | 0.0045576 | -8.42e-05 | -0.00047628 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpRes_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.805; coeff_2: 0.233; coeff_3: -0.038 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.827; coeff_2: 0.203; coeff_3: -0.03 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.852; coeff_2: 0.17; coeff_3: -0.0219 | [6 empty] | From .dat files included with MASControl2
SpltHP1SpRes_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 2.7312 | -0.10297 | 0.00093636 | 0.0047786 | -9.07e-05 | -0.00020282 | [10 empty] | From .dat files included with MASControl2
SpltHP1SpRes_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | 0.73905 | -0.0077897 | 0.0001283 | -0.00027 | 0.0006642 | -0.000648 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpRes_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0.90039 | 0.011087 | 0.0001701 | -0.025795 | 0.0008424 | -0.00029063 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP1SpRes_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0.93033 | -0.0064656 | 1.77e-05 | 0.028135 | -5.51e-06 | -0.00020866 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP2Sp_BF_fFlow | BF_fFlow | Linear |  | Flow |  | coeff_1: 1.75; coeff_2: -1578.5656 |  |  |  |  | 1 | 1.189 | From .dat files included with MASControl2
SpltHP2Sp_BF_fT | BF_fT | BiQuadratic |  | T | T | 20.0302 | -1.9228 | 0.051516 | 0.086184 | 0.0011502 | -0.0076788 | [8 empty] | 0 | 3.92 | From .dat files included with MASControl2
SpltHP2Sp_CEIR_fPLR_Hot | CEIR_fPLR_Hot | Cubic | EIRRatio | PLR |  | coeff_1: 0.00635; coeff_2: 1.12; coeff_3: -0.139; coeff_4: 0.016 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_CEIR_fPLR_Mod | CEIR_fPLR_Mod | Cubic | EIRRatio | PLR |  | coeff_1: -0.00144; coeff_2: 1.12; coeff_3: -0.14; coeff_4: 0.022 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_CEIR_fPLR_Tem | CEIR_fPLR_Tem | Cubic | EIRRatio | PLR |  | coeff_1: -0.00726; coeff_2: 1.11; coeff_3: -0.132; coeff_4: 0.0262 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_ClCap_fT | ClCap_fT | BiQuadratic |  | T | T | 1.524 | -0.066593 | 0.0029938 | 0.0016229 | -6.51e-05 | -0.00048924 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP2Sp_CLoss_fPLR_Hot | CLoss_fPLR_Hot | Quadratic |  | PLR |  | coeff_1: 0.923; coeff_2: 0.153; coeff_3: -0.0156 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_CLoss_fPLR_Mod | CLoss_fPLR_Mod | Quadratic |  | PLR |  | coeff_1: 0.94; coeff_2: 0.124; coeff_3: -0.0109 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_CLoss_fPLR_Tem | CLoss_fPLR_Tem | Quadratic |  | PLR |  | coeff_1: 0.959; coeff_2: 0.0934; coeff_3: -0.00688 | [6 empty] | From .dat files included with MASControl2
SpltHP2Sp_ClSH_fT | ClSH_fT | BiQuadratic |  | T | T | 1.54 | 0.038275 | -0.0029776 | -0.011491 | -0.00010044 | 0.0005346 | [10 empty] | From .dat files included with MASControl2
SpltHP2Sp_EIR_fT | EIR_fT | BiQuadratic | EIRRatio | T | T | -0.17251 | 0.11766 | -0.00324 | -0.01152 | 0.00077112 | -0.00057024 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP2Sp_HIR_fT | HIR_fT | BiQuadratic |  | T | T | 0.92729 | 0.0080201 | 0.00020153 | -0.021771 | 0.000729 | -0.00030326 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SpltHP2Sp_HtCap_fT | HtCap_fT | BiQuadratic |  | T | T | 0.87563 | -0.0046634 | 1.62e-14 | 0.02913 | 0.00012636 | -0.0001633 |  |  |  |  | 7.2222 | 29.4444 | -23.333 | 46.1111 |  |  | From .dat files included with MASControl2
SteamTurbine-Flow-fPSIG | SteamTurbineGen | BiQuadratic | QRatio | PSIG | PSIG | 38.7924 | -3.07e-05 | 1.11e-11 | 0.00014795 | 1.93e-11 | -7.36e-11 | [8 empty] | 18 | 100 | From .dat files included with MASControl2
SteamTurbine-HIR-fPLR | SteamTurbineGen | Quadratic |  | PLR |  | coeff_1: 0.12839; coeff_2: 0.9005; coeff_3: -0.028881 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Stippled_Optical-fAOI | PV-Module | Cubic |  | AOI |  | coeff_1: 4.7021; coeff_2: -0.21138; coeff_3: 0.0039323; coeff_4: -2.4e-05 | [6 empty] | From .dat files included with MASControl2
SWH-EFFFPLR-NECB2011 | Water Heater | Cubic | FIRRatio | QRatio |  | coeff_1: 0.7576; coeff_2: 1.0071; coeff_3: -1.4443; coeff_4: 0.6844 | 0 | 1 |  |  |  |  | From NECB 2011
Tower_Fan_Curve |  | Cubic |  |  |  | coeff_1: 0; coeff_2: 0; coeff_3: 0; coeff_4: 1 | 0 | 1 |  |  |  |  | From Prototype Buildings
Transformer-Loss-fPLR | ElecMeters | Linear | QRatio | PLR |  | coeff_1: 0.1; coeff_2: 0.9 | [6 empty] | From .dat files included with MASControl2
Two-Speed Fan EIR fPLR | FanEIR-FPLR | Linear |  | PLR |  | coeff_1: -0.76471; coeff_2: 1.7647 |  |  |  |  | 0.4 |  | From .dat files included with MASControl2
TwoSpeedFan | FanEIR-FPLR | Cubic | EIRRatio | PLR |  | coeff_1: 0.000281; coeff_2: -0.0579; coeff_3: 0.586; coeff_4: 0.471 | [6 empty] | From .dat files included with MASControl2
Typical VSD Fan | FanEIR-FPLR | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.047183; coeff_2: 0.13054; coeff_3: -0.11729; coeff_4: 0.94031 | 0 | 1 |  |  | 0.1 |  | From California Energy Commision, "Advanced Variable Air Volume System Design Guide," October 2003
TypicalCyclingAC-EIR-fPLR | CyclingAC | Cubic | EIRRatio | PLR |  | coeff_1: 6.26e-05; coeff_2: 1.1752; coeff_3: -0.20151; coeff_4: 0.026334 | [6 empty] | From .dat files included with MASControl2
Vane Axial w Var Pitch FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.21205; coeff_2: -0.56929; coeff_3: 1.3452 |  |  |  |  | 0.15 | 1 | From .dat files included with MASControl2
Variable Speed Drive FPLR | FanEIR-FPLR | Quadratic |  | PLR |  | coeff_1: 0.21976; coeff_2: -0.87478; coeff_3: 1.6526 |  |  |  |  | 0.1 | 1 | From .dat files included with MASControl2
VarVolFan-AFBIFanCurve-NECB2011-FPLR | Fan | Cubic | PwrRatio | FlowRatio |  | coeff_1: -2.4176; coeff_2: 9.5874; coeff_3: -11.559; coeff_4: 5.4009 | 0.68 | 1 |  |  |  |  | From NECB 2011
VarVolFan-AFBIInletVanes-NECB2011-FPLR | Fan | Cubic | PwrRatio | FlowRatio |  | coeff_1: -4.1457; coeff_2: 16.803; coeff_3: -19.471; coeff_4: 7.8488 | 0.5 | 1 |  |  |  |  | From NECB 2011
VarVolFan-FCInletVanes-NECB2011-FPLR | Fan | Cubic | PwrRatio | FlowRatio |  | coeff_1: -0.3477; coeff_2: 4.0976; coeff_3: -5.0024; coeff_4: 2.268 | 0.22 | 1 |  |  |  |  | From NECB 2011
VarVolFan-VSD-NECB2011-FPLR | Fan | Cubic | PwrRatio | FlowRatio |  | coeff_1: 0.1389; coeff_2: 1.7699; coeff_3: -1.615; coeff_4: 0.6996 | 0.04 | 1 |  |  |  |  | From NECB 2011
VFD-Loss-fPLR | Pumps | Linear | QRatio | PLR |  | coeff_1: 0.6; coeff_2: 0.4 | [6 empty] | From .dat files included with MASControl2
VRF-HP-Resys-ClCap-fSST&ODB | CondUnit | BiQuadratic | QRatio | SST | ODB | 1.2659 | 0 | 0 | -0.007582 | -2.14e-06 | 0 | [10 empty] | From .dat files included with MASControl2
VRF-HP-Resys-ClEIR-fSST&ODB | CondUnit | BiQuadratic | EIRRatio | SST | ODB | 0.38483 | 0 | 0 | 0.0092304 | 0.000238 | 0 | [10 empty] | From .dat files included with MASControl2
VRF-HP-Resys-Crankcase-fPLR | CondUnit | Quadratic |  | PLR |  | coeff_1: 1; coeff_2: -1.72; coeff_3: 0.72 | [6 empty] | From .dat files included with MASControl2
VRF-HP-Resys-Cycle-fPLR | CondUnit | Linear | QRatio | PLR |  | coeff_1: 0.898; coeff_2: 0.102 | [6 empty] | From .dat files included with MASControl2
VRF-HP-Resys-HtCap-fSCT&OWB | CondUnit | BiQuadratic | QRatio | SCT | OWB | 0.89783 | 0 | 0 | 0.016708 | 6.16e-07 | 0 | [10 empty] | From .dat files included with MASControl2
VRF-HP-Resys-HtEIR-fSCT&OWB | CondUnit | BiQuadratic | EIRRatio | SCT | OWB | 1.0525 | 0 | 0 | -0.0081569 | -8.72e-05 | 0 | [10 empty] | From .dat files included with MASControl2
VSD-TWR-FAN-FPLR | Cooling Tower | Cubic |  |  |  | coeff_1: 0.33163; coeff_2: -0.88568; coeff_3: 0.60557; coeff_4: 0.94848 | 0 | 1 |  |  |  |  | From PNNL PRM Reference Manual
Water-Cooled-Bypass-fAirflow | DXCooling,WCC | Cubic | QRatio | Airflow |  | coeff_1: 0.9; coeff_2: -3.73; coeff_3: 7.37; coeff_4: -3.54 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Water-Cooled-Bypass-fEWB&EWT | DXCooling,WCC | BiQuadratic | QRatio | EWB | EWT | -5.511 | 0.73564 | -0.0185 | 0.14252 | 0.000942 | -0.010213 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Water-Cooled-Cool-Cap-fEWB&EWT | DXCooling,WCC | BiQuadratic | QRatio | EWB | EWT | 0.82544 | 0.0057442 | 0.000735 | -0.0031037 | -1.46e-05 | -0.000194 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Water-Cooled-EIR-fEWB&EWT | DXCooling,WCC | BiQuadratic | EIRRatio | EWB | EWT | 0.098598 | 0.062604 | -0.0018436 | 0.01183 | 0.000292 | -0.000395 |  |  |  |  | 12.7778 | 29.4444 | 12.7778 | 46.1111 |  |  | From .dat files included with MASControl2
Water-Cooled-EIR-fPLR | DXCooling,WCC | Cubic | EIRRatio | PLR |  | coeff_1: 0.201; coeff_2: -0.0312; coeff_3: 1.9505; coeff_4: -1.1205 | 0 | 1.05 |  |  |  |  | From .dat files included with MASControl2
Water-Cooled-Sens-Cap-fEWB&EWT | DXCooling,WCC | BiQuadratic | QRatio | EWB | EWT | 2.1543 | -0.024278 | -0.0014872 | -0.0082955 | -2.96e-05 | 0.000272 |  |  |  |  | 12.7778 | 29.4444 | 10 | 46.1111 |  |  | From .dat files included with MASControl2
WaterCooled_Centrifugal_CAPFT_NECB2011 | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.70791 | -0.0020066 | -0.002596 | 0.030059 | -0.0010564 | 0.0020457 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Centrifugal_Chiller_150TO300_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_150TO300_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathA_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.53623 | 0.005581 | -0.0013654 | 0.048897 | -0.0012018 | 0.0010523 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_2010_PathB_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 1.0822 | 0.0042977 | -0.0013182 | -0.026078 | 0.0008256 | -0.0006013 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_300TO600_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_AllCapacities_2004_2007_2010_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010. EIRFPLR curve is identical for all WaterCooled Chillers
WaterCooled_Centrifugal_Chiller_GT150_2004_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.76002 | 0.014743 | 0.0002144 | 0.020722 | -0.0006425 | 0.0008007 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT150_2004_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.67726 | 0.011786 | -0.0001967 | 0.0014414 | 0.0003005 | -0.0006807 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT300_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_GT600_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.74465 | 0.011486 | 1.48e-05 | 0.022401 | -0.000688 | 0.0009839 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2004_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.77288 | 0.022101 | -7.99e-05 | -0.0070045 | 0.0004763 | -0.0010612 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_Chiller_LT150_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Centrifugal_EIRFPLR_NECB2011 | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.17149; coeff_2: 0.5882; coeff_3: 0.23737 | 0 | 1 |  |  |  |  | From NECB 2011
WaterCooled_Centrifugal_EIRFT_NECB2011 | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.56052 | -0.013782 | 6.5642e-05 | 0.013219 | 0.0002686 | -0.00050113 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_PositiveDisplacement_Chiller_150TO300_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_150TO300_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2004_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.90612 | 0.029227 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2004_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_2010_PathB_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_75TO150_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT150_2010_PathA_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.37731 | -0.022903 | 0.0016504 | 0.011816 | 0.0004345 | -0.0010132 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_GT300_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_CAPFT | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT150_2010_PathA_EIRFT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.36171 | -0.022983 | 0.0009519 | 0.013189 | 0.0003752 | -0.0007059 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2004_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathA_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_PositiveDisplacement_Chiller_LT75_2010_PathB_EIRFPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.13605 | 0.0086427 | 3.8556e-06 | 1.024 | 0.060474 | -0.0089479 | 0 | 0.057066 | 0 | 0 | 31.13 | 36.52 | 0.19 | 1.03 |  |  | Based on Dick Lord's study dated January 17, 2010.
WaterCooled_Reciprocating_CAPFT_NECB2011 | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 1.0303 | 0.03347 | 0.00023639 | -0.0072959 | -2.3166e-05 | -0.00014894 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Reciprocating_EIRFPLR_NECB2011 | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.081441; coeff_2: 0.41927; coeff_3: 0.4994 | 0 | 1 |  |  |  |  | From NECB 2011
WaterCooled_Reciprocating_EIRFT_NECB2011 | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.4997 | -0.013084 | 0.00026642 | 0.016592 | 0.00018539 | -0.00037565 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Screw_CAPFT_NECB2011 | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.813 | -0.014253 | -0.001618 | 0.026384 | -0.00091543 | 0.001696 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Screw_EIRFPLR_NECB2011 | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.33019; coeff_2: 0.23554; coeff_3: 0.46071 | 0 | 1 |  |  |  |  | From NECB 2011
WaterCooled_Screw_EIRFT_NECB2011 | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.6381 | 0.0063016 | 0.00092327 | -0.0045529 | 0.00082568 | -0.0015615 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Scroll_CAPFT_NECB2011 | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.94418 | 0.03371 | 9.7556e-05 | -0.0032211 | -4.9183e-05 | -0.00017758 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WaterCooled_Scroll_EIRFPLR_NECB2011 | Electric Chiller | Quadratic | EIRRatio | QRatio |  | coeff_1: 0.04412; coeff_2: 0.64037; coeff_3: 0.31955 | 0 | 1 |  |  |  |  | From NECB 2011
WaterCooled_Scroll_EIRFT_NECB2011 | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.72739 | -0.011892 | 0.00054118 | 0.0018793 | 0.00047346 | -0.00071147 |  |  |  |  | 5 | 10 | 24 | 35 |  |  | From NECB 2011
WC Screw Default 90.1-2004 Cap_fTWC | Electric Chiller | BiQuadratic | QRatio | Tchws | Toadb | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 |  |  |  |  | 0 | 20 | 0 | 50 |  |  | From RefBldgLargeOfficePost1980 & Pre1980
WC Screw Default 90.1-2004 EIR_fT | Electric Chiller | BiQuadratic | EIRRatio | Tchws | Toadb | 0.36171 | -0.022983 | -0.0009519 | 0.013189 | 0.0003752 | -0.0007059 |  |  |  |  | 0 | 20 | 0 | 50 |  |  | From RefBldgLargeOfficePost1980 % Pre1980
WC Screw GTE 300tons Default 90.1-2004 EIR_fPLR | Electric Chiller | BiCubic | EIRRatio | Tcws | QRatio | -0.2738 | 0.028223 | -8.0977e-05 | 0.96123 | 0.30297 | -0.024219 | 0 | -0.038852 | 0 | 0 | 18.54 | 31.63 | 0.2 | 1.02 |  |  | From RefBldgLargeOfficePost1980 & Pre1980
WC_PD_2004_CAPFT |  | BiQuadratic |  |  |  | 0.90612 | 0.029228 | -0.0003647 | -0.0009709 | -9.05e-05 | 0.0002527 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | From PNNL Prototype Hospital
WC_PD_2010_PB_CAPFT |  | BiQuadratic |  |  |  | 0.90612 | 0.029227 | -0.0003665 | -0.0009698 | -9.07e-05 | 0.0002535 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | From PNNL Prototype OfficeLarge
WC_PD_2010_PB_EIRFT |  | BiQuadratic |  |  |  | 0.36178 | -0.023002 | 0.0009672 | 0.01318 | 0.0003761 | -0.0007121 |  |  |  |  | 5 | 10 | 17.78 | 46.11 |  |  | From PNNL Prototype OfficeLarge
MT_compressor_power | Refrigeration | BiCubic | Power | Suction T | Discharge T | 7438.9223 | -269.5976 | -9.8561 | 553.5733 | -3.3859 | 14.8658 | -0.1008 | 0.0098228 | 0.097362 | -0.039675 | -23.3 | 7.2 | 10 | 60 |  |  | From AEDG
MT_compressor_capacity | Refrigeration | BiCubic | Capacity | Suction T | Discharge T | 151166.436 | 5266.3479 | 60.6727 | -1851.5594 | 5.7313 | -46.9277 | 0.1364 | -0.035698 | -0.40305 | -0.03929 | -23.3 | -7.2 | 10 | 60 |  |  | From AEDG
MT_compressor_capacity_smallandold | Refrigeration | BiCubic | Capacity | Suction T | Discharge T | 15000 | 541.8 | 7.285 | -118 | -0.3645 | -3.05 | 0.0344 | 0.00225 | -0.03927 | -0.007307 | -17.8 | 4.4 | 10 | 48.9 |  |  | From EP DataSets
MT_compressor_power_smallandold | Refrigeration | BiCubic | Power | Suction T | Discharge T | 483.6 | -53.2 | -1.384 | 56.19 | 0.003688 | 1.439 | -0.008268 | -0.00281 | 0.007222 | 0.006025 | -17.8 | 4.4 | 10 | 48.9 |  |  | From EP DataSets
LT_compressor_capacity_smallandold | Refrigeration | BiCubic | Capacity | Suction T | Discharge T | 23500 | 816.7 | 10.7 | -28.24 | 0.1131 | -0.4553 | 0.05604 | -0.00412 | -0.006728 | 0.006782 | -40 | -17.8 | 10 | 48.9 |  |  | From EP DataSets
LT_compressor_power_smallandold | Refrigeration | BiCubic | Power | Suction T | Discharge T | 4018 | 95 | 1.507 | 5.705 | 1.247 | -1.381 | 0.01277 | -0.007518 | -0.02424 | 0.02917 | -40 | -17.8 | 10 | 48.9 |  |  | From EP DataSets
Glass Door Latent Curve Case | Refrigeration | Cubic |  |  |  | coeff_1: 0.3379; coeff_2: 0.0309; coeff_3: 0.0005; coeff_4: 4e-05 | -55 | 55 |  |  |  |  | From AEDG
Coffin Latent Curve Case | Refrigeration | Cubic |  |  |  | coeff_1: 0.3379; coeff_2: 0.0309; coeff_3: 0.0005; coeff_4: 4e-05 | -55 | 55 |  |  |  |  | From AEDG
Open Latent Curve Case | Refrigeration | Cubic |  |  |  | coeff_1: -0.0187; coeff_2: 0.0458; coeff_3: 0.0011; coeff_4: 5e-05 | -55 | 55 |  |  |  |  | From AEDG
Glass Door Defrost Curve Walkin | Refrigeration | Cubic |  |  |  | coeff_1: 0.3475; coeff_2: 0.0296; coeff_3: 0.0007; coeff_4: 3e-05 | -55 | 55 |  |  |  |  | From AEDG
Coffin Defrost Curve Walkin | Refrigeration | Cubic |  |  |  | coeff_1: 0.3475; coeff_2: 0.0296; coeff_3: 0.0007; coeff_4: 3e-05 | -55 | 55 |  |  |  |  | From AEDG
Open Defrost Curve Walkin | Refrigeration | Cubic |  |  |  | coeff_1: 0.0572; coeff_2: 0.0461; coeff_3: 0.0004; coeff_4: 6e-05 | -55 | 55 |  |  |  |  | From AEDG
Refrigeration Case Latent Credit Curve | Refrigeration | Cubic |  |  |  | coeff_1: 0.026526; coeff_2: 0.001078; coeff_3: 6.0256e-05; coeff_4: 1.2373e-06 | -35 | 20

## Fans
Each row represents a specific type of fan
Name | Type | Pressure Rise (inH2O) | Fan Efficiency (fraction) | Motor Efficiency (fraction) | Motor In Airstream Fraction | Fan Power Minimum Flow Rate Fraction | Fan Power Minimum Flow Rate Input Method | Fan Curve | Notes
Constant_DOAS_Fan | ConstantVolume | 2.5 | 0.58175 | 0.895 | 1
CRAC_CAV_fan | ConstantVolume | 2.5 | 0.54 | 0.9 | 1
CRAC_Cycling_fan | OnOff | 2.5 | 0.54 | 0.9 | 1
CRAC_VAV_fan | VariableVolume | 1.2044 | 0.7 | 0.9 | 1 | 0.25 | Fraction | Single zone VAV fan
ERV_Exhaust_fan | OnOff | 0.25 | 0.44 | 0.8 | 1 |  |  |  | Assumes impeller efficiency of 0.55, 0.55*0.8 = 0.44
ERV_Supply_Fan | OnOff | 0.25 | 0.44 | 0.8 | 1 |  |  |  | Assumes impeller efficiency of 0.55, 0.55*0.8 = 0.44
Evap_Cooler_Supply_Fan | OnOff | 0.25 | 0.55
Fan_Coil_Fan | OnOff | 1.0876 | 0.16 | 0.29 | 1
Fan_Coil_VarSpeed_Fan | VariableVolume | 1.0876 | 0.16 | 0.29 | 1
Hospital_CAV_Sytem_Fan | ConstantVolume | 4.0885 | 0.61425 | 0.945 | 1
Minisplit_HP_Fan | OnOff | 0.1 | 0.168 | 1 | 1
Packaged_RTU_SZ_AC_CAV_Fan | ConstantVolume | 2.5 | 0.54 | 0.9 | 1
Packaged_RTU_SZ_AC_Cycling_Fan | OnOff | 2.5 | 0.54 | 0.9 | 1
PFP_Fan | ConstantVolume | 1.2044 |  |  | 1
PSZ_VAV_Fan | VariableVolume | 2.5 | 0.54 | 0.9 | 1 | 0.25 | Fraction | Single zone VAV fan
PTAC_CAV_Fan | ConstantVolume | 1.33 | 0.52 | 0.8 | 1
PTAC_Cycling_Fan | OnOff | 1.33 | 0.52 | 0.8 | 1
Residential_HVAC_Fan | OnOff | 0.5 | 0.6 | 1 | 1
Split_AC_CAV_Fan | ConstantVolume | 2.5 | 0.56 | 0.86 | 1
Split_AC_Cycling_Fan | OnOff | 2.5 | 0.53625 | 0.825 | 1
Unit_Heater_Fan | ConstantVolume |  | 0.53625 | 0.825 | 1
Variable_DOAS_Fan | VariableVolume | 2.5 | 0.58175 | 0.895 | 1 |  |  | Multi zone VAV with static pressure reset
VAV_default | VariableVolume | 4.0853 | 0.6045 | 0.93 | 1
VAV_System_Fan | VariableVolume | 2.5 | 0.54 | 0.9 | 1 | 0.25 | Fraction | Multi zone VAV with static pressure reset
Window_AC_Supply_Fan | OnOff | 0 | 1 | 1 | 0
WSHP_Fan | OnOff | 1.33 | 0.52 | 0.8 | 1

## Motors
Each row represents the efficiency standards for a specificy type of motor
Template | Number of Poles | Type | Synchronous Speed (RPM) | Minimum Capacity (HP) | Maximum Capacity (HP) | Nominal Full Load Efficiency (%) | Notes
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
DOE Ref Pre-1980 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
DOE Ref 1980-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2004 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2004 Table 10.8
90.1-2004 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2004 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2007 | 4 | Enclosed | 1800 | 1 | 1.499 | 82.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 2 | 2.999 | 84% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 3 | 4.999 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 5 | 7.499 | 87.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 10 | 14.999 | 89.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 15 | 19.999 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 20 | 24.999 | 91% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 25 | 29.999 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 30 | 39.999 | 92.4% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 40 | 49.999 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 50 | 59.999 | 93% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 60 | 74.999 | 93.6% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 75 | 99.999 | 94.1% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 100 | 124.999 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 125 | 149.999 | 94.5% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 150 | 199.999 | 95% | From 90.1-2007 Table 10.8
90.1-2007 | 4 | Enclosed | 1800 | 200 | 9999 | 95% | From 90.1-2007 Table 10.8
90.1-2010 | 4 | Enclosed | 1800 | 0 | 0.999 | 29% | Motors below 1 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2010 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 20 | 24.9999 | 93% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 60 | 74.999 | 95% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 250 | 299.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 300 | 349.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 350 | 399.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 400 | 449.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 450 | 499.999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2010 | 4 | Enclosed | 1800 | 500 | 9999 | 96.2% | From 90.1-2010 Table 10.8B
90.1-2013 | 4 | Enclosed | 1800 | 0 | 0.08333 | 29% | Motors below 1/12 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
90.1-2013 | 4 | Enclosed | 1800 | 0.08334 | 0.999 | 70% | Motors between 1/12 and 1 HP must be EC, with minimum efficiency of 70% per PNNL
90.1-2013 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5%
90.1-2013 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5%
90.1-2013 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5%
90.1-2013 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7%
90.1-2013 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4%
90.1-2013 | 4 | Enclosed | 1800 | 20 | 24.999 | 93%
90.1-2013 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6%
90.1-2013 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1%
90.1-2013 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5%
90.1-2013 | 4 | Enclosed | 1800 | 60 | 74.999 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8%
90.1-2013 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2%
90.1-2013 | 4 | Enclosed | 1800 | 250 | 299.999 | 95%
90.1-2013 | 4 | Enclosed | 1800 | 300 | 349.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 350 | 399.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 400 | 449.999 | 95.4%
90.1-2013 | 4 | Enclosed | 1800 | 450 | 499.999 | 0.954
90.1-2013 | 4 | Enclosed | 1800 | 500 | 9999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 0 | 0.08333 | 29% | Motors below 1/12 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
OEESC 2014 | 4 | Enclosed | 1800 | 0.08334 | 0.999 | 70% | Motors between 1/12 and 1 HP must be EC, with minimum efficiency of 70% per PNNL
OEESC 2014 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5%
OEESC 2014 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5%
OEESC 2014 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5%
OEESC 2014 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5%
OEESC 2014 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5%
OEESC 2014 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7%
OEESC 2014 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7%
OEESC 2014 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4%
OEESC 2014 | 4 | Enclosed | 1800 | 20 | 24.999 | 93%
OEESC 2014 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6%
OEESC 2014 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6%
OEESC 2014 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1%
OEESC 2014 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5%
OEESC 2014 | 4 | Enclosed | 1800 | 60 | 74.999 | 95%
OEESC 2014 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8%
OEESC 2014 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2%
OEESC 2014 | 4 | Enclosed | 1800 | 250 | 299.999 | 95%
OEESC 2014 | 4 | Enclosed | 1800 | 300 | 349.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 350 | 399.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 400 | 449.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 450 | 499.999 | 95.4%
OEESC 2014 | 4 | Enclosed | 1800 | 500 | 9999 | 95.4%
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 0 | 0.08333 | 29% | Same as 90.1-2013. Motors below 1/12 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 0.08334 | 0.999 | 70% | Same as 90.1-2013. Motors between 1/12 and 1 HP must be EC, with minimum efficiency of 70% per PNNL
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 20 | 24.999 | 93% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 60 | 74.999 | 95% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 250 | 299.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 300 | 349.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 350 | 399.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 400 | 449.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 450 | 499.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
NREL ZNE Ready 2017 | 4 | Enclosed | 1800 | 500 | 9999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 0 | 0.08333 | 29% | Same as 90.1-2013. Motors below 1/12 HP assumed to be PSC, with average typical efficiency of 29% per PNNL
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 0.08334 | 0.999 | 70% | Same as 90.1-2013. Motors between 1/12 and 1 HP must be EC, with minimum efficiency of 70% per PNNL
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 1 | 1.499 | 85.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 1.5 | 1.999 | 86.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 2 | 2.999 | 86.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 3 | 4.999 | 89.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 5 | 7.499 | 89.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 7.5 | 9.999 | 91.7% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 10 | 14.999 | 91.7% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 15 | 19.999 | 92.4% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 20 | 24.999 | 93% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 25 | 29.999 | 93.6% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 30 | 39.999 | 93.6% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 40 | 49.999 | 94.1% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 50 | 59.999 | 94.5% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 60 | 74.999 | 95% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 75 | 99.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 100 | 124.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 125 | 149.999 | 95.4% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 150 | 199.999 | 95.8% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 200 | 249.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 250 | 299.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 300 | 349.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 350 | 399.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 400 | 449.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 450 | 499.999 | 96.2% | Same as 90.1-2016 Table 10.8-1
ZE AEDG Multifamily | 4 | Enclosed | 1800 | 500 | 9999 | 96.2% | Same as 90.1-2016 Table 10.8-1

## Ground Temperatures
Ground temperatures at the building surface, created using the slab preprocessor with climate-specific slab insulation
Building Type | Template | Climate Zone | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-1A | 21.13 | 21.1 | 21.11 | 21.13 | 21.17 | 23.37 | 23.69 | 23.76 | 23.79 | 21.54 | 21.28 | 21.19
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Hospital | 90.1-2004 | ASHRAE 169-2013-1A | 21.03 | 21.01 | 21 | 21.01 | 21.02 | 23.16 | 23.51 | 23.59 | 23.62 | 21.43 | 21.15 | 21.08
LargeHotel | 90.1-2004 | ASHRAE 169-2013-1A | 20.99 | 20.97 | 20.99 | 21.01 | 21.04 | 21.06 | 21.1 | 21.11 | 21.11 | 21.09 | 21.06 | 21.03
LargeOffice | 90.1-2004 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
MediumOffice | 90.1-2004 | ASHRAE 169-2013-1A | 21.07 | 21.04 | 21.04 | 21.05 | 21.07 | 23.21 | 23.57 | 23.64 | 23.67 | 21.48 | 21.2 | 21.12
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Outpatient | 90.1-2004 | ASHRAE 169-2013-1A | 21.06 | 21.04 | 21.05 | 21.07 | 21.11 | 21.98 | 22.14 | 22.18 | 22.19 | 21.31 | 21.17 | 21.11
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-1A | 21.06 | 21.03 | 21.03 | 21.04 | 21.06 | 23.26 | 23.58 | 23.64 | 23.67 | 21.43 | 21.17 | 21.11
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-1A | 21.18 | 21.15 | 21.17 | 21.21 | 21.28 | 23.47 | 23.8 | 23.87 | 23.89 | 21.65 | 21.37 | 21.27
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-1A | 21.05 | 21.03 | 21.03 | 21.03 | 21.05 | 23.25 | 23.57 | 23.64 | 23.67 | 21.42 | 21.17 | 21.1
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-1A | 21.07 | 21.05 | 21.05 | 21.06 | 21.09 | 23.29 | 23.61 | 23.67 | 23.7 | 21.45 | 21.2 | 21.13
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.23 | 23.54 | 23.61 | 23.64 | 21.39 | 21.14 | 21.08
SmallHotel | 90.1-2004 | ASHRAE 169-2013-1A | 21.05 | 21.04 | 21.06 | 21.08 | 21.13 | 21.15 | 21.19 | 21.21 | 21.2 | 21.18 | 21.14 | 21.1
SmallOffice | 90.1-2004 | ASHRAE 169-2013-1A | 21.13 | 21.08 | 21.09 | 21.12 | 21.18 | 23.11 | 23.58 | 23.71 | 23.76 | 21.79 | 21.38 | 21.24
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
Warehouse | 90.1-2004 | ASHRAE 169-2013-1A | 22.62 | 22.7 | 23.01 | 23.52 | 24.7 | 25.42 | 26.34 | 26.65 | 26.55 | 25.99 | 24.79 | 23.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-1A | 21.13 | 21.1 | 21.11 | 21.13 | 21.17 | 23.37 | 23.69 | 23.76 | 23.79 | 21.54 | 21.28 | 21.19
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Hospital | 90.1-2007 | ASHRAE 169-2013-1A | 21.03 | 21.01 | 21 | 21.01 | 21.02 | 23.16 | 23.51 | 23.59 | 23.62 | 21.43 | 21.15 | 21.08
LargeHotel | 90.1-2007 | ASHRAE 169-2013-1A | 20.99 | 20.97 | 20.99 | 21.01 | 21.04 | 21.06 | 21.1 | 21.11 | 21.11 | 21.09 | 21.06 | 21.03
LargeOffice | 90.1-2007 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
MediumOffice | 90.1-2007 | ASHRAE 169-2013-1A | 21.07 | 21.04 | 21.04 | 21.05 | 21.07 | 23.21 | 23.57 | 23.64 | 23.67 | 21.48 | 21.2 | 21.12
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Outpatient | 90.1-2007 | ASHRAE 169-2013-1A | 21.06 | 21.04 | 21.05 | 21.07 | 21.11 | 21.98 | 22.14 | 22.18 | 22.19 | 21.31 | 21.17 | 21.11
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-1A | 21.06 | 21.03 | 21.03 | 21.04 | 21.06 | 23.26 | 23.58 | 23.64 | 23.67 | 21.43 | 21.17 | 21.11
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-1A | 21.18 | 21.15 | 21.17 | 21.21 | 21.28 | 23.47 | 23.8 | 23.87 | 23.89 | 21.65 | 21.37 | 21.27
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-1A | 21.05 | 21.03 | 21.03 | 21.03 | 21.05 | 23.25 | 23.57 | 23.64 | 23.67 | 21.42 | 21.17 | 21.1
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-1A | 21.07 | 21.05 | 21.05 | 21.06 | 21.09 | 23.29 | 23.61 | 23.67 | 23.7 | 21.45 | 21.2 | 21.13
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.23 | 23.54 | 23.61 | 23.64 | 21.39 | 21.14 | 21.08
SmallHotel | 90.1-2007 | ASHRAE 169-2013-1A | 21.05 | 21.04 | 21.06 | 21.08 | 21.13 | 21.15 | 21.19 | 21.21 | 21.2 | 21.18 | 21.14 | 21.1
SmallOffice | 90.1-2007 | ASHRAE 169-2013-1A | 21.13 | 21.08 | 21.09 | 21.12 | 21.18 | 23.11 | 23.58 | 23.71 | 23.76 | 21.79 | 21.38 | 21.24
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
Warehouse | 90.1-2007 | ASHRAE 169-2013-1A | 22.62 | 22.7 | 23.01 | 23.52 | 24.7 | 25.42 | 26.34 | 26.65 | 26.55 | 25.99 | 24.79 | 23.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-1A | 21.13 | 21.1 | 21.11 | 21.13 | 21.17 | 23.37 | 23.69 | 23.76 | 23.79 | 21.54 | 21.28 | 21.19
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Hospital | 90.1-2010 | ASHRAE 169-2013-1A | 21.03 | 21.01 | 21 | 21.01 | 21.02 | 23.16 | 23.51 | 23.59 | 23.62 | 21.43 | 21.15 | 21.08
LargeHotel | 90.1-2010 | ASHRAE 169-2013-1A | 20.99 | 20.97 | 20.99 | 21.01 | 21.04 | 21.06 | 21.1 | 21.11 | 21.11 | 21.09 | 21.06 | 21.03
LargeOffice | 90.1-2010 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
MediumOffice | 90.1-2010 | ASHRAE 169-2013-1A | 21.07 | 21.04 | 21.04 | 21.05 | 21.07 | 23.21 | 23.57 | 23.64 | 23.67 | 21.48 | 21.2 | 21.12
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Outpatient | 90.1-2010 | ASHRAE 169-2013-1A | 21.06 | 21.04 | 21.05 | 21.07 | 21.11 | 21.98 | 22.14 | 22.18 | 22.19 | 21.31 | 21.17 | 21.11
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-1A | 21.06 | 21.03 | 21.03 | 21.04 | 21.06 | 23.26 | 23.58 | 23.64 | 23.67 | 21.43 | 21.17 | 21.11
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-1A | 21.18 | 21.15 | 21.17 | 21.21 | 21.28 | 23.47 | 23.8 | 23.87 | 23.89 | 21.65 | 21.37 | 21.27
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-1A | 21.05 | 21.03 | 21.03 | 21.03 | 21.05 | 23.25 | 23.57 | 23.64 | 23.67 | 21.42 | 21.17 | 21.1
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-1A | 21.07 | 21.05 | 21.05 | 21.06 | 21.09 | 23.29 | 23.61 | 23.67 | 23.7 | 21.45 | 21.2 | 21.13
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.23 | 23.54 | 23.61 | 23.64 | 21.39 | 21.14 | 21.08
SmallHotel | 90.1-2010 | ASHRAE 169-2013-1A | 21.05 | 21.04 | 21.06 | 21.08 | 21.13 | 21.15 | 21.19 | 21.21 | 21.2 | 21.18 | 21.14 | 21.1
SmallOffice | 90.1-2010 | ASHRAE 169-2013-1A | 21.13 | 21.08 | 21.09 | 21.12 | 21.18 | 23.11 | 23.58 | 23.71 | 23.76 | 21.79 | 21.38 | 21.24
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
Warehouse | 90.1-2010 | ASHRAE 169-2013-1A | 22.62 | 22.7 | 23.01 | 23.52 | 24.7 | 25.42 | 26.34 | 26.65 | 26.55 | 25.99 | 24.79 | 23.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-1A | 21.13 | 21.1 | 21.11 | 21.13 | 21.17 | 23.37 | 23.69 | 23.76 | 23.79 | 21.54 | 21.28 | 21.19
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Hospital | 90.1-2013 | ASHRAE 169-2013-1A | 21.03 | 21.01 | 21 | 21.01 | 21.02 | 23.16 | 23.51 | 23.59 | 23.62 | 21.43 | 21.15 | 21.08
LargeHotel | 90.1-2013 | ASHRAE 169-2013-1A | 20.99 | 20.97 | 20.99 | 21.01 | 21.04 | 21.06 | 21.1 | 21.11 | 21.11 | 21.09 | 21.06 | 21.03
LargeOffice | 90.1-2013 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.17 | 23.52 | 23.59 | 23.62 | 21.44 | 21.15 | 21.09
MediumOffice | 90.1-2013 | ASHRAE 169-2013-1A | 21.07 | 21.04 | 21.04 | 21.05 | 21.07 | 23.21 | 23.57 | 23.64 | 23.67 | 21.48 | 21.2 | 21.12
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
Outpatient | 90.1-2013 | ASHRAE 169-2013-1A | 21.06 | 21.04 | 21.05 | 21.07 | 21.11 | 21.98 | 22.14 | 22.18 | 22.19 | 21.31 | 21.17 | 21.11
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-1A | 21.06 | 21.03 | 21.03 | 21.04 | 21.06 | 23.26 | 23.58 | 23.64 | 23.67 | 21.43 | 21.17 | 21.11
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-1A | 21.18 | 21.15 | 21.17 | 21.21 | 21.28 | 23.47 | 23.8 | 23.87 | 23.89 | 21.65 | 21.37 | 21.27
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-1A | 21.05 | 21.03 | 21.03 | 21.03 | 21.05 | 23.25 | 23.57 | 23.64 | 23.67 | 21.42 | 21.17 | 21.1
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-1A | 21.07 | 21.05 | 21.05 | 21.06 | 21.09 | 23.29 | 23.61 | 23.67 | 23.7 | 21.45 | 21.2 | 21.13
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-1A | 21.04 | 21.01 | 21.01 | 21.01 | 21.02 | 23.23 | 23.54 | 23.61 | 23.64 | 21.39 | 21.14 | 21.08
SmallHotel | 90.1-2013 | ASHRAE 169-2013-1A | 21.05 | 21.04 | 21.06 | 21.08 | 21.13 | 21.15 | 21.19 | 21.21 | 21.2 | 21.18 | 21.14 | 21.1
SmallOffice | 90.1-2013 | ASHRAE 169-2013-1A | 21.13 | 21.08 | 21.09 | 21.12 | 21.18 | 23.11 | 23.58 | 23.71 | 23.76 | 21.79 | 21.38 | 21.24
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
Warehouse | 90.1-2013 | ASHRAE 169-2013-1A | 22.62 | 22.7 | 23.01 | 23.52 | 24.7 | 25.42 | 26.34 | 26.65 | 26.55 | 25.99 | 24.79 | 23.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-1B | 20.8 | 20.84 | 21 | 21.21 | 21.38 | 23.63 | 23.86 | 23.85 | 23.84 | 21.57 | 21.19 | 20.95
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Hospital | 90.1-2004 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.11 | 23.27 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.99
LargeHotel | 90.1-2004 | ASHRAE 169-2013-1B | 20.76 | 20.78 | 20.89 | 21.05 | 21.19 | 21.26 | 21.23 | 21.19 | 21.16 | 21.13 | 21.02 | 20.86
LargeOffice | 90.1-2004 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
MediumOffice | 90.1-2004 | ASHRAE 169-2013-1B | 20.87 | 20.88 | 20.97 | 21.1 | 21.21 | 23.38 | 23.68 | 23.7 | 23.71 | 21.51 | 21.15 | 20.98
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Outpatient | 90.1-2004 | ASHRAE 169-2013-1B | 20.8 | 20.83 | 20.96 | 21.14 | 21.29 | 22.19 | 22.29 | 22.26 | 22.24 | 21.35 | 21.11 | 20.92
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-1B | 20.89 | 20.9 | 20.97 | 21.08 | 21.16 | 23.39 | 23.66 | 23.69 | 23.7 | 21.44 | 21.13 | 20.98
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-1B | 20.71 | 20.77 | 21.01 | 21.32 | 21.58 | 23.84 | 24.04 | 24 | 23.97 | 21.69 | 21.25 | 20.91
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.97 | 21.07 | 21.15 | 23.38 | 23.65 | 23.68 | 23.7 | 21.44 | 21.13 | 20.99
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-1B | 20.87 | 20.89 | 20.98 | 21.11 | 21.21 | 23.45 | 23.71 | 23.73 | 23.74 | 21.47 | 21.15 | 20.98
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-1B | 20.92 | 20.92 | 20.97 | 21.04 | 21.1 | 23.32 | 23.6 | 23.64 | 23.66 | 21.4 | 21.11 | 20.99
SmallHotel | 90.1-2004 | ASHRAE 169-2013-1B | 20.77 | 20.81 | 20.96 | 21.16 | 21.32 | 21.39 | 21.34 | 21.29 | 21.26 | 21.22 | 21.07 | 20.88
SmallOffice | 90.1-2004 | ASHRAE 169-2013-1B | 20.7 | 20.7 | 20.9 | 21.19 | 21.46 | 23.5 | 23.88 | 23.9 | 23.89 | 21.88 | 21.31 | 20.94
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
Warehouse | 90.1-2004 | ASHRAE 169-2013-1B | 14.11 | 16.78 | 21.39 | 27.32 | 31.3 | 32.42 | 31.15 | 29.72 | 28.54 | 25.45 | 20.51 | 15.65
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-1B | 20.8 | 20.84 | 21 | 21.21 | 21.38 | 23.63 | 23.86 | 23.85 | 23.84 | 21.57 | 21.19 | 20.95
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Hospital | 90.1-2007 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.11 | 23.27 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.99
LargeHotel | 90.1-2007 | ASHRAE 169-2013-1B | 20.76 | 20.78 | 20.89 | 21.05 | 21.19 | 21.26 | 21.23 | 21.19 | 21.16 | 21.13 | 21.02 | 20.86
LargeOffice | 90.1-2007 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
MediumOffice | 90.1-2007 | ASHRAE 169-2013-1B | 20.87 | 20.88 | 20.97 | 21.1 | 21.21 | 23.38 | 23.68 | 23.7 | 23.71 | 21.51 | 21.15 | 20.98
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Outpatient | 90.1-2007 | ASHRAE 169-2013-1B | 20.8 | 20.83 | 20.96 | 21.14 | 21.29 | 22.19 | 22.29 | 22.26 | 22.24 | 21.35 | 21.11 | 20.92
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-1B | 20.89 | 20.9 | 20.97 | 21.08 | 21.16 | 23.39 | 23.66 | 23.69 | 23.7 | 21.44 | 21.13 | 20.98
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-1B | 20.71 | 20.77 | 21.01 | 21.32 | 21.58 | 23.84 | 24.04 | 24 | 23.97 | 21.69 | 21.25 | 20.91
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.97 | 21.07 | 21.15 | 23.38 | 23.65 | 23.68 | 23.7 | 21.44 | 21.13 | 20.99
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-1B | 20.87 | 20.89 | 20.98 | 21.11 | 21.21 | 23.45 | 23.71 | 23.73 | 23.74 | 21.47 | 21.15 | 20.98
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-1B | 20.92 | 20.92 | 20.97 | 21.04 | 21.1 | 23.32 | 23.6 | 23.64 | 23.66 | 21.4 | 21.11 | 20.99
SmallHotel | 90.1-2007 | ASHRAE 169-2013-1B | 20.77 | 20.81 | 20.96 | 21.16 | 21.32 | 21.39 | 21.34 | 21.29 | 21.26 | 21.22 | 21.07 | 20.88
SmallOffice | 90.1-2007 | ASHRAE 169-2013-1B | 20.7 | 20.7 | 20.9 | 21.19 | 21.46 | 23.5 | 23.88 | 23.9 | 23.89 | 21.88 | 21.31 | 20.94
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
Warehouse | 90.1-2007 | ASHRAE 169-2013-1B | 14.11 | 16.78 | 21.39 | 27.32 | 31.3 | 32.42 | 31.15 | 29.72 | 28.54 | 25.45 | 20.51 | 15.65
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-1B | 20.8 | 20.84 | 21 | 21.21 | 21.38 | 23.63 | 23.86 | 23.85 | 23.84 | 21.57 | 21.19 | 20.95
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Hospital | 90.1-2010 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.11 | 23.27 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.99
LargeHotel | 90.1-2010 | ASHRAE 169-2013-1B | 20.76 | 20.78 | 20.89 | 21.05 | 21.19 | 21.26 | 21.23 | 21.19 | 21.16 | 21.13 | 21.02 | 20.86
LargeOffice | 90.1-2010 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
MediumOffice | 90.1-2010 | ASHRAE 169-2013-1B | 20.87 | 20.88 | 20.97 | 21.1 | 21.21 | 23.38 | 23.68 | 23.7 | 23.71 | 21.51 | 21.15 | 20.98
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Outpatient | 90.1-2010 | ASHRAE 169-2013-1B | 20.8 | 20.83 | 20.96 | 21.14 | 21.29 | 22.19 | 22.29 | 22.26 | 22.24 | 21.35 | 21.11 | 20.92
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-1B | 20.89 | 20.9 | 20.97 | 21.08 | 21.16 | 23.39 | 23.66 | 23.69 | 23.7 | 21.44 | 21.13 | 20.98
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-1B | 20.71 | 20.77 | 21.01 | 21.32 | 21.58 | 23.84 | 24.04 | 24 | 23.97 | 21.69 | 21.25 | 20.91
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.97 | 21.07 | 21.15 | 23.38 | 23.65 | 23.68 | 23.7 | 21.44 | 21.13 | 20.99
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-1B | 20.87 | 20.89 | 20.98 | 21.11 | 21.21 | 23.45 | 23.71 | 23.73 | 23.74 | 21.47 | 21.15 | 20.98
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-1B | 20.92 | 20.92 | 20.97 | 21.04 | 21.1 | 23.32 | 23.6 | 23.64 | 23.66 | 21.4 | 21.11 | 20.99
SmallHotel | 90.1-2010 | ASHRAE 169-2013-1B | 20.77 | 20.81 | 20.96 | 21.16 | 21.32 | 21.39 | 21.34 | 21.29 | 21.26 | 21.22 | 21.07 | 20.88
SmallOffice | 90.1-2010 | ASHRAE 169-2013-1B | 20.7 | 20.7 | 20.9 | 21.19 | 21.46 | 23.5 | 23.88 | 23.9 | 23.89 | 21.88 | 21.31 | 20.94
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
Warehouse | 90.1-2010 | ASHRAE 169-2013-1B | 14.11 | 16.78 | 21.39 | 27.32 | 31.3 | 32.42 | 31.15 | 29.72 | 28.54 | 25.45 | 20.51 | 15.65
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-1B | 20.8 | 20.84 | 21 | 21.21 | 21.38 | 23.63 | 23.86 | 23.85 | 23.84 | 21.57 | 21.19 | 20.95
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Hospital | 90.1-2013 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.11 | 23.27 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.99
LargeHotel | 90.1-2013 | ASHRAE 169-2013-1B | 20.76 | 20.78 | 20.89 | 21.05 | 21.19 | 21.26 | 21.23 | 21.19 | 21.16 | 21.13 | 21.02 | 20.86
LargeOffice | 90.1-2013 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.96 | 21.04 | 21.12 | 23.28 | 23.59 | 23.63 | 23.65 | 21.45 | 21.12 | 20.98
MediumOffice | 90.1-2013 | ASHRAE 169-2013-1B | 20.87 | 20.88 | 20.97 | 21.1 | 21.21 | 23.38 | 23.68 | 23.7 | 23.71 | 21.51 | 21.15 | 20.98
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
Outpatient | 90.1-2013 | ASHRAE 169-2013-1B | 20.8 | 20.83 | 20.96 | 21.14 | 21.29 | 22.19 | 22.29 | 22.26 | 22.24 | 21.35 | 21.11 | 20.92
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-1B | 20.89 | 20.9 | 20.97 | 21.08 | 21.16 | 23.39 | 23.66 | 23.69 | 23.7 | 21.44 | 21.13 | 20.98
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-1B | 20.71 | 20.77 | 21.01 | 21.32 | 21.58 | 23.84 | 24.04 | 24 | 23.97 | 21.69 | 21.25 | 20.91
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-1B | 20.9 | 20.9 | 20.97 | 21.07 | 21.15 | 23.38 | 23.65 | 23.68 | 23.7 | 21.44 | 21.13 | 20.99
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-1B | 20.87 | 20.89 | 20.98 | 21.11 | 21.21 | 23.45 | 23.71 | 23.73 | 23.74 | 21.47 | 21.15 | 20.98
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-1B | 20.92 | 20.92 | 20.97 | 21.04 | 21.1 | 23.32 | 23.6 | 23.64 | 23.66 | 21.4 | 21.11 | 20.99
SmallHotel | 90.1-2013 | ASHRAE 169-2013-1B | 20.77 | 20.81 | 20.96 | 21.16 | 21.32 | 21.39 | 21.34 | 21.29 | 21.26 | 21.22 | 21.07 | 20.88
SmallOffice | 90.1-2013 | ASHRAE 169-2013-1B | 20.7 | 20.7 | 20.9 | 21.19 | 21.46 | 23.5 | 23.88 | 23.9 | 23.89 | 21.88 | 21.31 | 20.94
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
Warehouse | 90.1-2013 | ASHRAE 169-2013-1B | 14.11 | 16.78 | 21.39 | 27.32 | 31.3 | 32.42 | 31.15 | 29.72 | 28.54 | 25.45 | 20.51 | 15.65
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.09 | 23.33 | 23.66 | 23.71 | 23.72 | 21.46 | 21.07 | 20.89
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Hospital | 90.1-2004 | ASHRAE 169-2013-2A | 20.87 | 20.86 | 20.87 | 20.91 | 20.99 | 23.15 | 23.5 | 23.56 | 23.59 | 21.4 | 21.07 | 20.95
LargeHotel | 90.1-2004 | ASHRAE 169-2013-2A | 20.69 | 20.7 | 20.73 | 20.82 | 20.96 | 21.02 | 21.06 | 21.07 | 21.06 | 21.03 | 20.91 | 20.8
LargeOffice | 90.1-2004 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.86 | 20.91 | 20.99 | 23.15 | 23.5 | 23.57 | 23.59 | 21.4 | 21.07 | 20.95
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-2A | 20.81 | 20.81 | 20.83 | 20.91 | 21.02 | 23.19 | 23.54 | 23.61 | 23.63 | 21.43 | 21.07 | 20.93
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Outpatient | 90.1-2004 | ASHRAE 169-2013-2A | 20.73 | 20.74 | 20.78 | 20.89 | 21.04 | 21.95 | 22.11 | 22.14 | 22.14 | 21.24 | 21 | 20.86
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-2A | 20.85 | 20.85 | 20.86 | 20.92 | 21.02 | 23.24 | 23.56 | 23.62 | 23.64 | 21.38 | 21.07 | 20.95
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-2A | 20.6 | 20.62 | 20.69 | 20.89 | 21.17 | 23.41 | 23.75 | 23.8 | 23.8 | 21.53 | 21.08 | 20.82
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.87 | 20.92 | 21.01 | 23.23 | 23.55 | 23.61 | 23.63 | 21.38 | 21.07 | 20.95
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-2A | 20.82 | 20.82 | 20.84 | 20.92 | 21.03 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.07 | 20.93
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-2A | 20.89 | 20.88 | 20.89 | 20.93 | 20.99 | 23.21 | 23.53 | 23.59 | 23.61 | 21.36 | 21.07 | 20.97
SmallHotel | 90.1-2004 | ASHRAE 169-2013-2A | 20.69 | 20.71 | 20.76 | 20.88 | 21.05 | 21.12 | 21.16 | 21.16 | 21.15 | 21.1 | 20.95 | 20.82
SmallOffice | 90.1-2004 | ASHRAE 169-2013-2A | 20.59 | 20.57 | 20.62 | 20.79 | 21.05 | 23.06 | 23.56 | 23.66 | 23.69 | 21.69 | 21.13 | 20.84
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
Warehouse | 90.1-2004 | ASHRAE 169-2013-2A | 14.26 | 15.51 | 16.91 | 20.32 | 25.35 | 26.63 | 27.13 | 26.88 | 25.95 | 24.24 | 19.64 | 16.43
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.09 | 23.33 | 23.66 | 23.71 | 23.72 | 21.46 | 21.07 | 20.89
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Hospital | 90.1-2007 | ASHRAE 169-2013-2A | 20.87 | 20.86 | 20.87 | 20.91 | 20.99 | 23.15 | 23.5 | 23.56 | 23.59 | 21.4 | 21.07 | 20.95
LargeHotel | 90.1-2007 | ASHRAE 169-2013-2A | 20.69 | 20.7 | 20.73 | 20.82 | 20.96 | 21.02 | 21.06 | 21.07 | 21.06 | 21.03 | 20.91 | 20.8
LargeOffice | 90.1-2007 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.86 | 20.91 | 20.99 | 23.15 | 23.5 | 23.57 | 23.59 | 21.4 | 21.07 | 20.95
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-2A | 20.81 | 20.81 | 20.83 | 20.91 | 21.02 | 23.19 | 23.54 | 23.61 | 23.63 | 21.43 | 21.07 | 20.93
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Outpatient | 90.1-2007 | ASHRAE 169-2013-2A | 20.73 | 20.74 | 20.78 | 20.89 | 21.04 | 21.95 | 22.11 | 22.14 | 22.14 | 21.24 | 21 | 20.86
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-2A | 20.85 | 20.85 | 20.86 | 20.92 | 21.02 | 23.24 | 23.56 | 23.62 | 23.64 | 21.38 | 21.07 | 20.95
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-2A | 20.6 | 20.62 | 20.69 | 20.89 | 21.17 | 23.41 | 23.75 | 23.8 | 23.8 | 21.53 | 21.08 | 20.82
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.87 | 20.92 | 21.01 | 23.23 | 23.55 | 23.61 | 23.63 | 21.38 | 21.07 | 20.95
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-2A | 20.82 | 20.82 | 20.84 | 20.92 | 21.03 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.07 | 20.93
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-2A | 20.89 | 20.88 | 20.89 | 20.93 | 20.99 | 23.21 | 23.53 | 23.59 | 23.61 | 21.36 | 21.07 | 20.97
SmallHotel | 90.1-2007 | ASHRAE 169-2013-2A | 20.69 | 20.71 | 20.76 | 20.88 | 21.05 | 21.12 | 21.16 | 21.16 | 21.15 | 21.1 | 20.95 | 20.82
SmallOffice | 90.1-2007 | ASHRAE 169-2013-2A | 20.59 | 20.57 | 20.62 | 20.79 | 21.05 | 23.06 | 23.56 | 23.66 | 23.69 | 21.69 | 21.13 | 20.84
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
Warehouse | 90.1-2007 | ASHRAE 169-2013-2A | 14.26 | 15.51 | 16.91 | 20.32 | 25.35 | 26.63 | 27.13 | 26.88 | 25.95 | 24.24 | 19.64 | 16.43
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.09 | 23.33 | 23.66 | 23.71 | 23.72 | 21.46 | 21.07 | 20.89
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Hospital | 90.1-2010 | ASHRAE 169-2013-2A | 20.87 | 20.86 | 20.87 | 20.91 | 20.99 | 23.15 | 23.5 | 23.56 | 23.59 | 21.4 | 21.07 | 20.95
LargeHotel | 90.1-2010 | ASHRAE 169-2013-2A | 20.69 | 20.7 | 20.73 | 20.82 | 20.96 | 21.02 | 21.06 | 21.07 | 21.06 | 21.03 | 20.91 | 20.8
LargeOffice | 90.1-2010 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.86 | 20.91 | 20.99 | 23.15 | 23.5 | 23.57 | 23.59 | 21.4 | 21.07 | 20.95
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-2A | 20.81 | 20.81 | 20.83 | 20.91 | 21.02 | 23.19 | 23.54 | 23.61 | 23.63 | 21.43 | 21.07 | 20.93
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Outpatient | 90.1-2010 | ASHRAE 169-2013-2A | 20.73 | 20.74 | 20.78 | 20.89 | 21.04 | 21.95 | 22.11 | 22.14 | 22.14 | 21.24 | 21 | 20.86
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-2A | 20.85 | 20.85 | 20.86 | 20.92 | 21.02 | 23.24 | 23.56 | 23.62 | 23.64 | 21.38 | 21.07 | 20.95
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-2A | 20.6 | 20.62 | 20.69 | 20.89 | 21.17 | 23.41 | 23.75 | 23.8 | 23.8 | 21.53 | 21.08 | 20.82
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.87 | 20.92 | 21.01 | 23.23 | 23.55 | 23.61 | 23.63 | 21.38 | 21.07 | 20.95
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-2A | 20.82 | 20.82 | 20.84 | 20.92 | 21.03 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.07 | 20.93
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-2A | 20.89 | 20.88 | 20.89 | 20.93 | 20.99 | 23.21 | 23.53 | 23.59 | 23.61 | 21.36 | 21.07 | 20.97
SmallHotel | 90.1-2010 | ASHRAE 169-2013-2A | 20.69 | 20.71 | 20.76 | 20.88 | 21.05 | 21.12 | 21.16 | 21.16 | 21.15 | 21.1 | 20.95 | 20.82
SmallOffice | 90.1-2010 | ASHRAE 169-2013-2A | 20.59 | 20.57 | 20.62 | 20.79 | 21.05 | 23.06 | 23.56 | 23.66 | 23.69 | 21.69 | 21.13 | 20.84
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
Warehouse | 90.1-2010 | ASHRAE 169-2013-2A | 14.26 | 15.51 | 16.91 | 20.32 | 25.35 | 26.63 | 27.13 | 26.88 | 25.95 | 24.24 | 19.64 | 16.43
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.09 | 23.33 | 23.66 | 23.71 | 23.72 | 21.46 | 21.07 | 20.89
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Hospital | 90.1-2013 | ASHRAE 169-2013-2A | 20.87 | 20.86 | 20.87 | 20.91 | 20.99 | 23.15 | 23.5 | 23.56 | 23.59 | 21.4 | 21.07 | 20.95
LargeHotel | 90.1-2013 | ASHRAE 169-2013-2A | 20.69 | 20.7 | 20.73 | 20.82 | 20.96 | 21.02 | 21.06 | 21.07 | 21.06 | 21.03 | 20.91 | 20.8
LargeOffice | 90.1-2013 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.86 | 20.91 | 20.99 | 23.15 | 23.5 | 23.57 | 23.59 | 21.4 | 21.07 | 20.95
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-2A | 20.81 | 20.81 | 20.83 | 20.91 | 21.02 | 23.19 | 23.54 | 23.61 | 23.63 | 21.43 | 21.07 | 20.93
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
Outpatient | 90.1-2013 | ASHRAE 169-2013-2A | 20.73 | 20.74 | 20.78 | 20.89 | 21.04 | 21.95 | 22.11 | 22.14 | 22.14 | 21.24 | 21 | 20.86
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-2A | 20.85 | 20.85 | 20.86 | 20.92 | 21.02 | 23.24 | 23.56 | 23.62 | 23.64 | 21.38 | 21.07 | 20.95
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-2A | 20.6 | 20.62 | 20.69 | 20.89 | 21.17 | 23.41 | 23.75 | 23.8 | 23.8 | 21.53 | 21.08 | 20.82
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-2A | 20.86 | 20.85 | 20.87 | 20.92 | 21.01 | 23.23 | 23.55 | 23.61 | 23.63 | 21.38 | 21.07 | 20.95
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-2A | 20.82 | 20.82 | 20.84 | 20.92 | 21.03 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.07 | 20.93
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-2A | 20.89 | 20.88 | 20.89 | 20.93 | 20.99 | 23.21 | 23.53 | 23.59 | 23.61 | 21.36 | 21.07 | 20.97
SmallHotel | 90.1-2013 | ASHRAE 169-2013-2A | 20.69 | 20.71 | 20.76 | 20.88 | 21.05 | 21.12 | 21.16 | 21.16 | 21.15 | 21.1 | 20.95 | 20.82
SmallOffice | 90.1-2013 | ASHRAE 169-2013-2A | 20.59 | 20.57 | 20.62 | 20.79 | 21.05 | 23.06 | 23.56 | 23.66 | 23.69 | 21.69 | 21.13 | 20.84
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
Warehouse | 90.1-2013 | ASHRAE 169-2013-2A | 14.26 | 15.51 | 16.91 | 20.32 | 25.35 | 26.63 | 27.13 | 26.88 | 25.95 | 24.24 | 19.64 | 16.43
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-2B | 20.73 | 20.66 | 20.71 | 20.94 | 21.09 | 23.44 | 23.77 | 23.83 | 23.82 | 21.43 | 20.98 | 20.72
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Hospital | 90.1-2004 | ASHRAE 169-2013-2B | 20.87 | 20.83 | 20.84 | 20.92 | 20.98 | 23.19 | 23.54 | 23.61 | 23.63 | 21.38 | 21.03 | 20.89
LargeHotel | 90.1-2004 | ASHRAE 169-2013-2B | 20.68 | 20.64 | 20.68 | 20.83 | 20.96 | 21.09 | 21.14 | 21.16 | 21.13 | 21.01 | 20.84 | 20.68
LargeOffice | 90.1-2004 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.83 | 20.92 | 20.99 | 23.19 | 23.55 | 23.62 | 23.64 | 21.38 | 21.02 | 20.88
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2B
MediumOffice | 90.1-2004 | ASHRAE 169-2013-2B | 20.81 | 20.77 | 20.79 | 20.92 | 21.02 | 23.25 | 23.61 | 23.68 | 23.69 | 21.41 | 21.01 | 20.83
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Outpatient | 90.1-2004 | ASHRAE 169-2013-2B | 20.73 | 20.68 | 20.72 | 20.91 | 21.04 | 22.03 | 22.2 | 22.24 | 22.22 | 21.22 | 20.92 | 20.72
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-2B | 20.85 | 20.81 | 20.83 | 20.94 | 21.01 | 23.29 | 23.61 | 23.68 | 23.69 | 21.37 | 21.02 | 20.87
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-2B | 20.61 | 20.52 | 20.6 | 20.94 | 21.17 | 23.58 | 23.92 | 23.98 | 23.94 | 21.48 | 20.93 | 20.59
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.84 | 20.94 | 21.01 | 23.28 | 23.61 | 23.67 | 23.68 | 21.36 | 21.02 | 20.88
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-2B | 20.82 | 20.78 | 20.8 | 20.94 | 21.03 | 23.33 | 23.65 | 23.72 | 23.72 | 21.38 | 21.01 | 20.83
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-2B | 20.89 | 20.86 | 20.87 | 20.94 | 20.99 | 23.25 | 23.57 | 23.63 | 23.65 | 21.35 | 21.03 | 20.91
SmallHotel | 90.1-2004 | ASHRAE 169-2013-2B | 20.69 | 20.64 | 20.7 | 20.9 | 21.05 | 21.21 | 21.26 | 21.27 | 21.23 | 21.07 | 20.86 | 20.67
SmallOffice | 90.1-2004 | ASHRAE 169-2013-2B | 20.54 | 20.45 | 20.5 | 20.79 | 21.03 | 23.17 | 23.69 | 23.82 | 23.82 | 21.66 | 20.99 | 20.6
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
Warehouse | 90.1-2004 | ASHRAE 169-2013-2B | 14.92 | 13.3 | 15.21 | 21.72 | 25.01 | 29.43 | 29.51 | 29.15 | 27.59 | 21.72 | 16.49 | 13.64
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-2B | 20.73 | 20.66 | 20.71 | 20.94 | 21.09 | 23.44 | 23.77 | 23.83 | 23.82 | 21.43 | 20.98 | 20.72
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Hospital | 90.1-2007 | ASHRAE 169-2013-2B | 20.87 | 20.83 | 20.84 | 20.92 | 20.98 | 23.19 | 23.54 | 23.61 | 23.63 | 21.38 | 21.03 | 20.89
LargeHotel | 90.1-2007 | ASHRAE 169-2013-2B | 20.68 | 20.64 | 20.68 | 20.83 | 20.96 | 21.09 | 21.14 | 21.16 | 21.13 | 21.01 | 20.84 | 20.68
LargeOffice | 90.1-2007 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.83 | 20.92 | 20.99 | 23.19 | 23.55 | 23.62 | 23.64 | 21.38 | 21.02 | 20.88
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2B
MediumOffice | 90.1-2007 | ASHRAE 169-2013-2B | 20.81 | 20.77 | 20.79 | 20.92 | 21.02 | 23.25 | 23.61 | 23.68 | 23.69 | 21.41 | 21.01 | 20.83
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Outpatient | 90.1-2007 | ASHRAE 169-2013-2B | 20.73 | 20.68 | 20.72 | 20.91 | 21.04 | 22.03 | 22.2 | 22.24 | 22.22 | 21.22 | 20.92 | 20.72
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-2B | 20.85 | 20.81 | 20.83 | 20.94 | 21.01 | 23.29 | 23.61 | 23.68 | 23.69 | 21.37 | 21.02 | 20.87
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-2B | 20.61 | 20.52 | 20.6 | 20.94 | 21.17 | 23.58 | 23.92 | 23.98 | 23.94 | 21.48 | 20.93 | 20.59
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.84 | 20.94 | 21.01 | 23.28 | 23.61 | 23.67 | 23.68 | 21.36 | 21.02 | 20.88
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-2B | 20.82 | 20.78 | 20.8 | 20.94 | 21.03 | 23.33 | 23.65 | 23.72 | 23.72 | 21.38 | 21.01 | 20.83
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-2B | 20.89 | 20.86 | 20.87 | 20.94 | 20.99 | 23.25 | 23.57 | 23.63 | 23.65 | 21.35 | 21.03 | 20.91
SmallHotel | 90.1-2007 | ASHRAE 169-2013-2B | 20.69 | 20.64 | 20.7 | 20.9 | 21.05 | 21.21 | 21.26 | 21.27 | 21.23 | 21.07 | 20.86 | 20.67
SmallOffice | 90.1-2007 | ASHRAE 169-2013-2B | 20.54 | 20.45 | 20.5 | 20.79 | 21.03 | 23.17 | 23.69 | 23.82 | 23.82 | 21.66 | 20.99 | 20.6
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
Warehouse | 90.1-2007 | ASHRAE 169-2013-2B | 14.92 | 13.3 | 15.21 | 21.72 | 25.01 | 29.43 | 29.51 | 29.15 | 27.59 | 21.72 | 16.49 | 13.64
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-2B | 20.73 | 20.66 | 20.71 | 20.94 | 21.09 | 23.44 | 23.77 | 23.83 | 23.82 | 21.43 | 20.98 | 20.72
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Hospital | 90.1-2010 | ASHRAE 169-2013-2B | 20.87 | 20.83 | 20.84 | 20.92 | 20.98 | 23.19 | 23.54 | 23.61 | 23.63 | 21.38 | 21.03 | 20.89
LargeHotel | 90.1-2010 | ASHRAE 169-2013-2B | 20.68 | 20.64 | 20.68 | 20.83 | 20.96 | 21.09 | 21.14 | 21.16 | 21.13 | 21.01 | 20.84 | 20.68
LargeOffice | 90.1-2010 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.83 | 20.92 | 20.99 | 23.19 | 23.55 | 23.62 | 23.64 | 21.38 | 21.02 | 20.88
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2B
MediumOffice | 90.1-2010 | ASHRAE 169-2013-2B | 20.81 | 20.77 | 20.79 | 20.92 | 21.02 | 23.25 | 23.61 | 23.68 | 23.69 | 21.41 | 21.01 | 20.83
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Outpatient | 90.1-2010 | ASHRAE 169-2013-2B | 20.73 | 20.68 | 20.72 | 20.91 | 21.04 | 22.03 | 22.2 | 22.24 | 22.22 | 21.22 | 20.92 | 20.72
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-2B | 20.85 | 20.81 | 20.83 | 20.94 | 21.01 | 23.29 | 23.61 | 23.68 | 23.69 | 21.37 | 21.02 | 20.87
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-2B | 20.61 | 20.52 | 20.6 | 20.94 | 21.17 | 23.58 | 23.92 | 23.98 | 23.94 | 21.48 | 20.93 | 20.59
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.84 | 20.94 | 21.01 | 23.28 | 23.61 | 23.67 | 23.68 | 21.36 | 21.02 | 20.88
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-2B | 20.82 | 20.78 | 20.8 | 20.94 | 21.03 | 23.33 | 23.65 | 23.72 | 23.72 | 21.38 | 21.01 | 20.83
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-2B | 20.89 | 20.86 | 20.87 | 20.94 | 20.99 | 23.25 | 23.57 | 23.63 | 23.65 | 21.35 | 21.03 | 20.91
SmallHotel | 90.1-2010 | ASHRAE 169-2013-2B | 20.69 | 20.64 | 20.7 | 20.9 | 21.05 | 21.21 | 21.26 | 21.27 | 21.23 | 21.07 | 20.86 | 20.67
SmallOffice | 90.1-2010 | ASHRAE 169-2013-2B | 20.54 | 20.45 | 20.5 | 20.79 | 21.03 | 23.17 | 23.69 | 23.82 | 23.82 | 21.66 | 20.99 | 20.6
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
Warehouse | 90.1-2010 | ASHRAE 169-2013-2B | 14.92 | 13.3 | 15.21 | 21.72 | 25.01 | 29.43 | 29.51 | 29.15 | 27.59 | 21.72 | 16.49 | 13.64
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-2B | 20.73 | 20.66 | 20.71 | 20.94 | 21.09 | 23.44 | 23.77 | 23.83 | 23.82 | 21.43 | 20.98 | 20.72
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Hospital | 90.1-2013 | ASHRAE 169-2013-2B | 20.87 | 20.83 | 20.84 | 20.92 | 20.98 | 23.19 | 23.54 | 23.61 | 23.63 | 21.38 | 21.03 | 20.89
LargeHotel | 90.1-2013 | ASHRAE 169-2013-2B | 20.68 | 20.64 | 20.68 | 20.83 | 20.96 | 21.09 | 21.14 | 21.16 | 21.13 | 21.01 | 20.84 | 20.68
LargeOffice | 90.1-2013 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.83 | 20.92 | 20.99 | 23.19 | 23.55 | 23.62 | 23.64 | 21.38 | 21.02 | 20.88
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2B
MediumOffice | 90.1-2013 | ASHRAE 169-2013-2B | 20.81 | 20.77 | 20.79 | 20.92 | 21.02 | 23.25 | 23.61 | 23.68 | 23.69 | 21.41 | 21.01 | 20.83
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
Outpatient | 90.1-2013 | ASHRAE 169-2013-2B | 20.73 | 20.68 | 20.72 | 20.91 | 21.04 | 22.03 | 22.2 | 22.24 | 22.22 | 21.22 | 20.92 | 20.72
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-2B | 20.85 | 20.81 | 20.83 | 20.94 | 21.01 | 23.29 | 23.61 | 23.68 | 23.69 | 21.37 | 21.02 | 20.87
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-2B | 20.61 | 20.52 | 20.6 | 20.94 | 21.17 | 23.58 | 23.92 | 23.98 | 23.94 | 21.48 | 20.93 | 20.59
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-2B | 20.86 | 20.82 | 20.84 | 20.94 | 21.01 | 23.28 | 23.61 | 23.67 | 23.68 | 21.36 | 21.02 | 20.88
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-2B | 20.82 | 20.78 | 20.8 | 20.94 | 21.03 | 23.33 | 23.65 | 23.72 | 23.72 | 21.38 | 21.01 | 20.83
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-2B | 20.89 | 20.86 | 20.87 | 20.94 | 20.99 | 23.25 | 23.57 | 23.63 | 23.65 | 21.35 | 21.03 | 20.91
SmallHotel | 90.1-2013 | ASHRAE 169-2013-2B | 20.69 | 20.64 | 20.7 | 20.9 | 21.05 | 21.21 | 21.26 | 21.27 | 21.23 | 21.07 | 20.86 | 20.67
SmallOffice | 90.1-2013 | ASHRAE 169-2013-2B | 20.54 | 20.45 | 20.5 | 20.79 | 21.03 | 23.17 | 23.69 | 23.82 | 23.82 | 21.66 | 20.99 | 20.6
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
Warehouse | 90.1-2013 | ASHRAE 169-2013-2B | 14.92 | 13.3 | 15.21 | 21.72 | 25.01 | 29.43 | 29.51 | 29.15 | 27.59 | 21.72 | 16.49 | 13.64
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3A | 20.26 | 20.28 | 20.5 | 20.65 | 20.81 | 23.13 | 23.52 | 23.61 | 23.55 | 21.17 | 20.73 | 20.48
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Hospital | 90.1-2004 | ASHRAE 169-2013-3A | 20.67 | 20.67 | 20.75 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeHotel | 90.1-2004 | ASHRAE 169-2013-3A | 20.34 | 20.35 | 20.5 | 20.62 | 20.73 | 20.86 | 20.94 | 20.98 | 20.93 | 20.79 | 20.64 | 20.49
LargeOffice | 90.1-2004 | ASHRAE 169-2013-3A | 20.66 | 20.66 | 20.74 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-3A | 20.52 | 20.52 | 20.65 | 20.74 | 20.84 | 23.05 | 23.45 | 23.54 | 23.52 | 21.25 | 20.85 | 20.67
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Outpatient | 90.1-2004 | ASHRAE 169-2013-3A | 20.35 | 20.36 | 20.54 | 20.67 | 20.8 | 21.78 | 22 | 22.05 | 22 | 20.99 | 20.71 | 20.52
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-3A | 20.62 | 20.62 | 20.72 | 20.79 | 20.87 | 23.13 | 23.49 | 23.56 | 23.55 | 21.24 | 20.9 | 20.74
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3A | 19.93 | 19.97 | 20.3 | 20.53 | 20.76 | 23.13 | 23.56 | 23.66 | 23.56 | 21.11 | 20.59 | 20.24
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-3A | 20.64 | 20.63 | 20.73 | 20.8 | 20.87 | 23.13 | 23.48 | 23.56 | 23.55 | 21.24 | 20.9 | 20.76
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-3A | 20.53 | 20.54 | 20.67 | 20.76 | 20.85 | 23.13 | 23.49 | 23.57 | 23.55 | 21.22 | 20.86 | 20.68
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-3A | 20.72 | 20.72 | 20.79 | 20.84 | 20.89 | 23.13 | 23.48 | 23.55 | 23.55 | 21.25 | 20.94 | 20.82
SmallHotel | 90.1-2004 | ASHRAE 169-2013-3A | 20.27 | 20.29 | 20.5 | 20.64 | 20.78 | 20.94 | 21.03 | 21.07 | 21 | 20.82 | 20.63 | 20.44
SmallOffice | 90.1-2004 | ASHRAE 169-2013-3A | 19.94 | 19.91 | 20.19 | 20.41 | 20.63 | 22.75 | 23.34 | 23.5 | 23.47 | 21.3 | 20.66 | 20.27
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
Warehouse | 90.1-2004 | ASHRAE 169-2013-3A | 12.91 | 12.85 | 13.71 | 16.52 | 19.78 | 23.45 | 25.07 | 25.69 | 22.62 | 16.89 | 13.58 | 13.1
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3A | 20.26 | 20.28 | 20.5 | 20.65 | 20.81 | 23.13 | 23.52 | 23.61 | 23.55 | 21.17 | 20.73 | 20.48
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Hospital | 90.1-2007 | ASHRAE 169-2013-3A | 20.67 | 20.67 | 20.75 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeHotel | 90.1-2007 | ASHRAE 169-2013-3A | 20.34 | 20.35 | 20.5 | 20.62 | 20.73 | 20.86 | 20.94 | 20.98 | 20.93 | 20.79 | 20.64 | 20.49
LargeOffice | 90.1-2007 | ASHRAE 169-2013-3A | 20.66 | 20.66 | 20.74 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-3A | 20.52 | 20.52 | 20.65 | 20.74 | 20.84 | 23.05 | 23.45 | 23.54 | 23.52 | 21.25 | 20.85 | 20.67
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Outpatient | 90.1-2007 | ASHRAE 169-2013-3A | 20.35 | 20.36 | 20.54 | 20.67 | 20.8 | 21.78 | 22 | 22.05 | 22 | 20.99 | 20.71 | 20.52
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-3A | 20.62 | 20.62 | 20.72 | 20.79 | 20.87 | 23.13 | 23.49 | 23.56 | 23.55 | 21.24 | 20.9 | 20.74
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3A | 19.93 | 19.97 | 20.3 | 20.53 | 20.76 | 23.13 | 23.56 | 23.66 | 23.56 | 21.11 | 20.59 | 20.24
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-3A | 20.64 | 20.63 | 20.73 | 20.8 | 20.87 | 23.13 | 23.48 | 23.56 | 23.55 | 21.24 | 20.9 | 20.76
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-3A | 20.53 | 20.54 | 20.67 | 20.76 | 20.85 | 23.13 | 23.49 | 23.57 | 23.55 | 21.22 | 20.86 | 20.68
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-3A | 20.72 | 20.72 | 20.79 | 20.84 | 20.89 | 23.13 | 23.48 | 23.55 | 23.55 | 21.25 | 20.94 | 20.82
SmallHotel | 90.1-2007 | ASHRAE 169-2013-3A | 20.27 | 20.29 | 20.5 | 20.64 | 20.78 | 20.94 | 21.03 | 21.07 | 21 | 20.82 | 20.63 | 20.44
SmallOffice | 90.1-2007 | ASHRAE 169-2013-3A | 19.94 | 19.91 | 20.19 | 20.41 | 20.63 | 22.75 | 23.34 | 23.5 | 23.47 | 21.3 | 20.66 | 20.27
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
Warehouse | 90.1-2007 | ASHRAE 169-2013-3A | 12.91 | 12.85 | 13.71 | 16.52 | 19.78 | 23.45 | 25.07 | 25.69 | 22.62 | 16.89 | 13.58 | 13.1
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3A | 20.26 | 20.28 | 20.5 | 20.65 | 20.81 | 23.13 | 23.52 | 23.61 | 23.55 | 21.17 | 20.73 | 20.48
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Hospital | 90.1-2010 | ASHRAE 169-2013-3A | 20.67 | 20.67 | 20.75 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeHotel | 90.1-2010 | ASHRAE 169-2013-3A | 20.34 | 20.35 | 20.5 | 20.62 | 20.73 | 20.86 | 20.94 | 20.98 | 20.93 | 20.79 | 20.64 | 20.49
LargeOffice | 90.1-2010 | ASHRAE 169-2013-3A | 20.66 | 20.66 | 20.74 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-3A | 20.52 | 20.52 | 20.65 | 20.74 | 20.84 | 23.05 | 23.45 | 23.54 | 23.52 | 21.25 | 20.85 | 20.67
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-3A | 20.25 | 20.27 | 20.49 | 20.64 | 20.79 | 23.05 | 23.48 | 23.57 | 23.52 | 21.2 | 20.73 | 20.48
Outpatient | 90.1-2010 | ASHRAE 169-2013-3A | 20.35 | 20.36 | 20.54 | 20.67 | 20.8 | 21.78 | 22 | 22.05 | 22 | 20.99 | 20.71 | 20.52
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-3A | 20.62 | 20.62 | 20.72 | 20.79 | 20.87 | 23.13 | 23.49 | 23.56 | 23.55 | 21.24 | 20.9 | 20.74
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3A | 19.93 | 19.97 | 20.3 | 20.53 | 20.76 | 23.13 | 23.56 | 23.66 | 23.56 | 21.11 | 20.59 | 20.24
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-3A | 20.64 | 20.63 | 20.73 | 20.8 | 20.87 | 23.13 | 23.48 | 23.56 | 23.55 | 21.24 | 20.9 | 20.76
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-3A | 20.53 | 20.54 | 20.67 | 20.76 | 20.85 | 23.13 | 23.49 | 23.57 | 23.55 | 21.22 | 20.86 | 20.68
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-3A | 20.72 | 20.72 | 20.79 | 20.84 | 20.89 | 23.13 | 23.48 | 23.55 | 23.55 | 21.25 | 20.94 | 20.82
SmallHotel | 90.1-2010 | ASHRAE 169-2013-3A | 20.27 | 20.29 | 20.5 | 20.64 | 20.78 | 20.94 | 21.03 | 21.07 | 21 | 20.82 | 20.63 | 20.44
SmallOffice | 90.1-2010 | ASHRAE 169-2013-3A | 19.94 | 19.91 | 20.19 | 20.41 | 20.63 | 22.75 | 23.34 | 23.5 | 23.47 | 21.3 | 20.66 | 20.27
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
Warehouse | 90.1-2010 | ASHRAE 169-2013-3A | 12.91 | 12.85 | 13.71 | 16.52 | 19.78 | 23.45 | 25.07 | 25.69 | 22.62 | 16.89 | 13.58 | 13.1
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3A | 20.26 | 20.28 | 20.5 | 20.65 | 20.81 | 23.13 | 23.52 | 23.61 | 23.55 | 21.17 | 20.73 | 20.48
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-3A | 20.51 | 20.47 | 20.58 | 20.67 | 20.76 | 22.99 | 23.41 | 23.51 | 23.52 | 21.26 | 20.86 | 20.68
Hospital | 90.1-2013 | ASHRAE 169-2013-3A | 20.67 | 20.67 | 20.75 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeHotel | 90.1-2013 | ASHRAE 169-2013-3A | 20.34 | 20.35 | 20.5 | 20.62 | 20.73 | 20.86 | 20.94 | 20.98 | 20.93 | 20.79 | 20.64 | 20.49
LargeOffice | 90.1-2013 | ASHRAE 169-2013-3A | 20.66 | 20.66 | 20.74 | 20.8 | 20.86 | 23.06 | 23.44 | 23.52 | 23.52 | 21.27 | 20.92 | 20.78
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-3A | 20.52 | 20.52 | 20.65 | 20.74 | 20.84 | 23.05 | 23.45 | 23.54 | 23.52 | 21.25 | 20.85 | 20.67
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-3A | 20.51 | 20.47 | 20.58 | 20.67 | 20.76 | 22.99 | 23.41 | 23.51 | 23.52 | 21.26 | 20.86 | 20.68
Outpatient | 90.1-2013 | ASHRAE 169-2013-3A | 20.35 | 20.36 | 20.54 | 20.67 | 20.8 | 21.78 | 22 | 22.05 | 22 | 20.99 | 20.71 | 20.52
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-3A | 20.62 | 20.62 | 20.72 | 20.79 | 20.87 | 23.13 | 23.49 | 23.56 | 23.55 | 21.24 | 20.9 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3A | 19.93 | 19.97 | 20.3 | 20.53 | 20.76 | 23.13 | 23.56 | 23.66 | 23.56 | 21.11 | 20.59 | 20.24
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-3A | 20.64 | 20.63 | 20.73 | 20.8 | 20.87 | 23.13 | 23.48 | 23.56 | 23.55 | 21.24 | 20.9 | 20.76
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-3A | 20.53 | 20.54 | 20.67 | 20.76 | 20.85 | 23.13 | 23.49 | 23.57 | 23.55 | 21.22 | 20.86 | 20.68
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-3A | 20.72 | 20.72 | 20.79 | 20.84 | 20.89 | 23.13 | 23.48 | 23.55 | 23.55 | 21.25 | 20.94 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2013-3A | 20.27 | 20.29 | 20.5 | 20.64 | 20.78 | 20.94 | 21.03 | 21.07 | 21 | 20.82 | 20.63 | 20.44
SmallOffice | 90.1-2013 | ASHRAE 169-2013-3A | 19.94 | 19.91 | 20.19 | 20.41 | 20.63 | 22.75 | 23.34 | 23.5 | 23.47 | 21.3 | 20.66 | 20.27
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
Warehouse | 90.1-2013 | ASHRAE 169-2013-3A | 12.91 | 12.85 | 13.71 | 16.52 | 19.78 | 23.45 | 25.07 | 25.69 | 22.62 | 16.89 | 13.58 | 13.1
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3B | 20.44 | 20.45 | 20.53 | 20.73 | 20.94 | 23.3 | 23.63 | 23.7 | 23.67 | 21.3 | 20.81 | 20.53
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Hospital | 90.1-2004 | ASHRAE 169-2013-3B | 20.75 | 20.74 | 20.76 | 20.84 | 20.92 | 23.13 | 23.48 | 23.55 | 23.57 | 21.33 | 20.96 | 20.81
LargeHotel | 90.1-2004 | ASHRAE 169-2013-3B | 20.47 | 20.48 | 20.54 | 20.67 | 20.83 | 20.99 | 21.03 | 21.05 | 21.01 | 20.9 | 20.71 | 20.53
LargeOffice | 90.1-2004 | ASHRAE 169-2013-3B | 20.74 | 20.73 | 20.75 | 20.83 | 20.92 | 23.13 | 23.49 | 23.56 | 23.57 | 21.33 | 20.95 | 20.8
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3B
MediumOffice | 90.1-2004 | ASHRAE 169-2013-3B | 20.63 | 20.63 | 20.67 | 20.79 | 20.92 | 23.17 | 23.52 | 23.59 | 23.59 | 21.33 | 20.91 | 20.71
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Outpatient | 90.1-2004 | ASHRAE 169-2013-3B | 20.49 | 20.51 | 20.57 | 20.74 | 20.91 | 21.92 | 22.09 | 22.13 | 22.09 | 21.1 | 20.78 | 20.56
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-3B | 20.71 | 20.7 | 20.74 | 20.83 | 20.94 | 23.22 | 23.54 | 23.61 | 23.61 | 21.3 | 20.94 | 20.77
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3B | 20.19 | 20.22 | 20.34 | 20.64 | 20.95 | 23.38 | 23.72 | 23.79 | 23.72 | 21.3 | 20.7 | 20.31
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-3B | 20.72 | 20.72 | 20.75 | 20.84 | 20.94 | 23.22 | 23.54 | 23.6 | 23.61 | 21.3 | 20.94 | 20.78
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-3B | 20.64 | 20.65 | 20.69 | 20.81 | 20.94 | 23.24 | 23.56 | 23.63 | 23.62 | 21.3 | 20.91 | 20.71
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-3B | 20.79 | 20.78 | 20.8 | 20.86 | 20.94 | 23.2 | 23.52 | 23.58 | 23.59 | 21.3 | 20.97 | 20.84
SmallHotel | 90.1-2004 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.53 | 20.71 | 20.91 | 21.09 | 21.13 | 21.15 | 21.1 | 20.95 | 20.71 | 20.49
SmallOffice | 90.1-2004 | ASHRAE 169-2013-3B | 20.17 | 20.16 | 20.25 | 20.51 | 20.82 | 22.99 | 23.5 | 23.64 | 23.62 | 21.47 | 20.78 | 20.35
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
Warehouse | 90.1-2004 | ASHRAE 169-2013-3B | 13.02 | 12.94 | 12.92 | 18.03 | 22.41 | 26.33 | 26.64 | 25.84 | 23.47 | 18.98 | 13.86 | 13.19
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3B | 20.44 | 20.45 | 20.53 | 20.73 | 20.94 | 23.3 | 23.63 | 23.7 | 23.67 | 21.3 | 20.81 | 20.53
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Hospital | 90.1-2007 | ASHRAE 169-2013-3B | 20.75 | 20.74 | 20.76 | 20.84 | 20.92 | 23.13 | 23.48 | 23.55 | 23.57 | 21.33 | 20.96 | 20.81
LargeHotel | 90.1-2007 | ASHRAE 169-2013-3B | 20.47 | 20.48 | 20.54 | 20.67 | 20.83 | 20.99 | 21.03 | 21.05 | 21.01 | 20.9 | 20.71 | 20.53
LargeOffice | 90.1-2007 | ASHRAE 169-2013-3B | 20.74 | 20.73 | 20.75 | 20.83 | 20.92 | 23.13 | 23.49 | 23.56 | 23.57 | 21.33 | 20.95 | 20.8
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3B
MediumOffice | 90.1-2007 | ASHRAE 169-2013-3B | 20.63 | 20.63 | 20.67 | 20.79 | 20.92 | 23.17 | 23.52 | 23.59 | 23.59 | 21.33 | 20.91 | 20.71
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Outpatient | 90.1-2007 | ASHRAE 169-2013-3B | 20.49 | 20.51 | 20.57 | 20.74 | 20.91 | 21.92 | 22.09 | 22.13 | 22.09 | 21.1 | 20.78 | 20.56
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-3B | 20.71 | 20.7 | 20.74 | 20.83 | 20.94 | 23.22 | 23.54 | 23.61 | 23.61 | 21.3 | 20.94 | 20.77
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3B | 20.19 | 20.22 | 20.34 | 20.64 | 20.95 | 23.38 | 23.72 | 23.79 | 23.72 | 21.3 | 20.7 | 20.31
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-3B | 20.72 | 20.72 | 20.75 | 20.84 | 20.94 | 23.22 | 23.54 | 23.6 | 23.61 | 21.3 | 20.94 | 20.78
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-3B | 20.64 | 20.65 | 20.69 | 20.81 | 20.94 | 23.24 | 23.56 | 23.63 | 23.62 | 21.3 | 20.91 | 20.71
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-3B | 20.79 | 20.78 | 20.8 | 20.86 | 20.94 | 23.2 | 23.52 | 23.58 | 23.59 | 21.3 | 20.97 | 20.84
SmallHotel | 90.1-2007 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.53 | 20.71 | 20.91 | 21.09 | 21.13 | 21.15 | 21.1 | 20.95 | 20.71 | 20.49
SmallOffice | 90.1-2007 | ASHRAE 169-2013-3B | 20.17 | 20.16 | 20.25 | 20.51 | 20.82 | 22.99 | 23.5 | 23.64 | 23.62 | 21.47 | 20.78 | 20.35
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
Warehouse | 90.1-2007 | ASHRAE 169-2013-3B | 13.02 | 12.94 | 12.92 | 18.03 | 22.41 | 26.33 | 26.64 | 25.84 | 23.47 | 18.98 | 13.86 | 13.19
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3B | 20.44 | 20.45 | 20.53 | 20.73 | 20.94 | 23.3 | 23.63 | 23.7 | 23.67 | 21.3 | 20.81 | 20.53
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Hospital | 90.1-2010 | ASHRAE 169-2013-3B | 20.75 | 20.74 | 20.76 | 20.84 | 20.92 | 23.13 | 23.48 | 23.55 | 23.57 | 21.33 | 20.96 | 20.81
LargeHotel | 90.1-2010 | ASHRAE 169-2013-3B | 20.47 | 20.48 | 20.54 | 20.67 | 20.83 | 20.99 | 21.03 | 21.05 | 21.01 | 20.9 | 20.71 | 20.53
LargeOffice | 90.1-2010 | ASHRAE 169-2013-3B | 20.74 | 20.73 | 20.75 | 20.83 | 20.92 | 23.13 | 23.49 | 23.56 | 23.57 | 21.33 | 20.95 | 20.8
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3B
MediumOffice | 90.1-2010 | ASHRAE 169-2013-3B | 20.63 | 20.63 | 20.67 | 20.79 | 20.92 | 23.17 | 23.52 | 23.59 | 23.59 | 21.33 | 20.91 | 20.71
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.52 | 20.72 | 20.93 | 23.23 | 23.59 | 23.66 | 23.64 | 21.33 | 20.82 | 20.53
Outpatient | 90.1-2010 | ASHRAE 169-2013-3B | 20.49 | 20.51 | 20.57 | 20.74 | 20.91 | 21.92 | 22.09 | 22.13 | 22.09 | 21.1 | 20.78 | 20.56
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-3B | 20.71 | 20.7 | 20.74 | 20.83 | 20.94 | 23.22 | 23.54 | 23.61 | 23.61 | 21.3 | 20.94 | 20.77
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3B | 20.19 | 20.22 | 20.34 | 20.64 | 20.95 | 23.38 | 23.72 | 23.79 | 23.72 | 21.3 | 20.7 | 20.31
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-3B | 20.72 | 20.72 | 20.75 | 20.84 | 20.94 | 23.22 | 23.54 | 23.6 | 23.61 | 21.3 | 20.94 | 20.78
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-3B | 20.64 | 20.65 | 20.69 | 20.81 | 20.94 | 23.24 | 23.56 | 23.63 | 23.62 | 21.3 | 20.91 | 20.71
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-3B | 20.79 | 20.78 | 20.8 | 20.86 | 20.94 | 23.2 | 23.52 | 23.58 | 23.59 | 21.3 | 20.97 | 20.84
SmallHotel | 90.1-2010 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.53 | 20.71 | 20.91 | 21.09 | 21.13 | 21.15 | 21.1 | 20.95 | 20.71 | 20.49
SmallOffice | 90.1-2010 | ASHRAE 169-2013-3B | 20.17 | 20.16 | 20.25 | 20.51 | 20.82 | 22.99 | 23.5 | 23.64 | 23.62 | 21.47 | 20.78 | 20.35
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
Warehouse | 90.1-2010 | ASHRAE 169-2013-3B | 13.02 | 12.94 | 12.92 | 18.03 | 22.41 | 26.33 | 26.64 | 25.84 | 23.47 | 18.98 | 13.86 | 13.19
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3B | 20.44 | 20.45 | 20.53 | 20.73 | 20.94 | 23.3 | 23.63 | 23.7 | 23.67 | 21.3 | 20.81 | 20.53
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-3B | 20.62 | 20.6 | 20.62 | 20.72 | 20.85 | 23.12 | 23.5 | 23.59 | 23.6 | 21.35 | 20.94 | 20.73
Hospital | 90.1-2013 | ASHRAE 169-2013-3B | 20.75 | 20.74 | 20.76 | 20.84 | 20.92 | 23.13 | 23.48 | 23.55 | 23.57 | 21.33 | 20.96 | 20.81
LargeHotel | 90.1-2013 | ASHRAE 169-2013-3B | 20.47 | 20.48 | 20.54 | 20.67 | 20.83 | 20.99 | 21.03 | 21.05 | 21.01 | 20.9 | 20.71 | 20.53
LargeOffice | 90.1-2013 | ASHRAE 169-2013-3B | 20.74 | 20.73 | 20.75 | 20.83 | 20.92 | 23.13 | 23.49 | 23.56 | 23.57 | 21.33 | 20.95 | 20.8
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3B
MediumOffice | 90.1-2013 | ASHRAE 169-2013-3B | 20.63 | 20.63 | 20.67 | 20.79 | 20.92 | 23.17 | 23.52 | 23.59 | 23.59 | 21.33 | 20.91 | 20.71
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-3B | 20.62 | 20.6 | 20.62 | 20.72 | 20.85 | 23.12 | 23.5 | 23.59 | 23.6 | 21.35 | 20.94 | 20.73
Outpatient | 90.1-2013 | ASHRAE 169-2013-3B | 20.49 | 20.51 | 20.57 | 20.74 | 20.91 | 21.92 | 22.09 | 22.13 | 22.09 | 21.1 | 20.78 | 20.56
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-3B | 20.71 | 20.7 | 20.74 | 20.83 | 20.94 | 23.22 | 23.54 | 23.61 | 23.61 | 21.3 | 20.94 | 20.77
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3B | 20.19 | 20.22 | 20.34 | 20.64 | 20.95 | 23.38 | 23.72 | 23.79 | 23.72 | 21.3 | 20.7 | 20.31
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-3B | 20.72 | 20.72 | 20.75 | 20.84 | 20.94 | 23.22 | 23.54 | 23.6 | 23.61 | 21.3 | 20.94 | 20.78
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-3B | 20.64 | 20.65 | 20.69 | 20.81 | 20.94 | 23.24 | 23.56 | 23.63 | 23.62 | 21.3 | 20.91 | 20.71
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-3B | 20.79 | 20.78 | 20.8 | 20.86 | 20.94 | 23.2 | 23.52 | 23.58 | 23.59 | 21.3 | 20.97 | 20.84
SmallHotel | 90.1-2013 | ASHRAE 169-2013-3B | 20.43 | 20.45 | 20.53 | 20.71 | 20.91 | 21.09 | 21.13 | 21.15 | 21.1 | 20.95 | 20.71 | 20.49
SmallOffice | 90.1-2013 | ASHRAE 169-2013-3B | 20.17 | 20.16 | 20.25 | 20.51 | 20.82 | 22.99 | 23.5 | 23.64 | 23.62 | 21.47 | 20.78 | 20.35
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
Warehouse | 90.1-2013 | ASHRAE 169-2013-3B | 13.02 | 12.94 | 12.92 | 18.03 | 22.41 | 26.33 | 26.64 | 25.84 | 23.47 | 18.98 | 13.86 | 13.19
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3C | 20.56 | 20.56 | 20.54 | 20.63 | 20.67 | 22.88 | 23.26 | 23.35 | 23.31 | 21.13 | 20.75 | 20.63
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Hospital | 90.1-2004 | ASHRAE 169-2013-3C | 20.8 | 20.78 | 20.77 | 20.79 | 20.81 | 22.96 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeHotel | 90.1-2004 | ASHRAE 169-2013-3C | 20.55 | 20.55 | 20.54 | 20.6 | 20.64 | 20.69 | 20.76 | 20.79 | 20.75 | 20.74 | 20.65 | 20.58
LargeOffice | 90.1-2004 | ASHRAE 169-2013-3C | 20.79 | 20.78 | 20.76 | 20.79 | 20.81 | 22.95 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3C
MediumOffice | 90.1-2004 | ASHRAE 169-2013-3C | 20.71 | 20.7 | 20.68 | 20.73 | 20.76 | 22.9 | 23.29 | 23.38 | 23.37 | 21.22 | 20.87 | 20.77
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Outpatient | 90.1-2004 | ASHRAE 169-2013-3C | 20.59 | 20.59 | 20.58 | 20.65 | 20.69 | 21.58 | 21.79 | 21.85 | 21.81 | 20.95 | 20.73 | 20.64
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-3C | 20.77 | 20.76 | 20.74 | 20.78 | 20.8 | 23.01 | 23.35 | 23.43 | 23.43 | 21.21 | 20.9 | 20.82
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-3C | 20.38 | 20.38 | 20.36 | 20.49 | 20.56 | 22.77 | 23.18 | 23.28 | 23.21 | 21.05 | 20.61 | 20.46
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-3C | 20.78 | 20.77 | 20.75 | 20.79 | 20.81 | 23.01 | 23.36 | 23.43 | 23.44 | 21.22 | 20.91 | 20.83
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-3C | 20.72 | 20.71 | 20.69 | 20.74 | 20.77 | 22.98 | 23.33 | 23.41 | 23.4 | 21.19 | 20.87 | 20.77
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-3C | 20.83 | 20.82 | 20.8 | 20.83 | 20.84 | 23.05 | 23.38 | 23.45 | 23.46 | 21.24 | 20.95 | 20.87
SmallHotel | 90.1-2004 | ASHRAE 169-2013-3C | 20.54 | 20.55 | 20.54 | 20.62 | 20.67 | 20.73 | 20.82 | 20.85 | 20.8 | 20.78 | 20.65 | 20.58
SmallOffice | 90.1-2004 | ASHRAE 169-2013-3C | 20.36 | 20.34 | 20.32 | 20.42 | 20.5 | 22.45 | 23 | 23.16 | 23.14 | 21.22 | 20.69 | 20.48
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
Warehouse | 90.1-2004 | ASHRAE 169-2013-3C | 13.38 | 13.38 | 12.92 | 14.88 | 15.38 | 17.13 | 18.76 | 19.25 | 18.38 | 18.54 | 14.85 | 13.86
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3C | 20.56 | 20.56 | 20.54 | 20.63 | 20.67 | 22.88 | 23.26 | 23.35 | 23.31 | 21.13 | 20.75 | 20.63
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Hospital | 90.1-2007 | ASHRAE 169-2013-3C | 20.8 | 20.78 | 20.77 | 20.79 | 20.81 | 22.96 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeHotel | 90.1-2007 | ASHRAE 169-2013-3C | 20.55 | 20.55 | 20.54 | 20.6 | 20.64 | 20.69 | 20.76 | 20.79 | 20.75 | 20.74 | 20.65 | 20.58
LargeOffice | 90.1-2007 | ASHRAE 169-2013-3C | 20.79 | 20.78 | 20.76 | 20.79 | 20.81 | 22.95 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3C
MediumOffice | 90.1-2007 | ASHRAE 169-2013-3C | 20.71 | 20.7 | 20.68 | 20.73 | 20.76 | 22.9 | 23.29 | 23.38 | 23.37 | 21.22 | 20.87 | 20.77
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Outpatient | 90.1-2007 | ASHRAE 169-2013-3C | 20.59 | 20.59 | 20.58 | 20.65 | 20.69 | 21.58 | 21.79 | 21.85 | 21.81 | 20.95 | 20.73 | 20.64
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-3C | 20.77 | 20.76 | 20.74 | 20.78 | 20.8 | 23.01 | 23.35 | 23.43 | 23.43 | 21.21 | 20.9 | 20.82
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-3C | 20.38 | 20.38 | 20.36 | 20.49 | 20.56 | 22.77 | 23.18 | 23.28 | 23.21 | 21.05 | 20.61 | 20.46
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-3C | 20.78 | 20.77 | 20.75 | 20.79 | 20.81 | 23.01 | 23.36 | 23.43 | 23.44 | 21.22 | 20.91 | 20.83
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-3C | 20.72 | 20.71 | 20.69 | 20.74 | 20.77 | 22.98 | 23.33 | 23.41 | 23.4 | 21.19 | 20.87 | 20.77
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-3C | 20.83 | 20.82 | 20.8 | 20.83 | 20.84 | 23.05 | 23.38 | 23.45 | 23.46 | 21.24 | 20.95 | 20.87
SmallHotel | 90.1-2007 | ASHRAE 169-2013-3C | 20.54 | 20.55 | 20.54 | 20.62 | 20.67 | 20.73 | 20.82 | 20.85 | 20.8 | 20.78 | 20.65 | 20.58
SmallOffice | 90.1-2007 | ASHRAE 169-2013-3C | 20.36 | 20.34 | 20.32 | 20.42 | 20.5 | 22.45 | 23 | 23.16 | 23.14 | 21.22 | 20.69 | 20.48
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
Warehouse | 90.1-2007 | ASHRAE 169-2013-3C | 13.38 | 13.38 | 12.92 | 14.88 | 15.38 | 17.13 | 18.76 | 19.25 | 18.38 | 18.54 | 14.85 | 13.86
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3C | 20.56 | 20.56 | 20.54 | 20.63 | 20.67 | 22.88 | 23.26 | 23.35 | 23.31 | 21.13 | 20.75 | 20.63
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Hospital | 90.1-2010 | ASHRAE 169-2013-3C | 20.8 | 20.78 | 20.77 | 20.79 | 20.81 | 22.96 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeHotel | 90.1-2010 | ASHRAE 169-2013-3C | 20.55 | 20.55 | 20.54 | 20.6 | 20.64 | 20.69 | 20.76 | 20.79 | 20.75 | 20.74 | 20.65 | 20.58
LargeOffice | 90.1-2010 | ASHRAE 169-2013-3C | 20.79 | 20.78 | 20.76 | 20.79 | 20.81 | 22.95 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3C
MediumOffice | 90.1-2010 | ASHRAE 169-2013-3C | 20.71 | 20.7 | 20.68 | 20.73 | 20.76 | 22.9 | 23.29 | 23.38 | 23.37 | 21.22 | 20.87 | 20.77
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-3C | 20.56 | 20.55 | 20.53 | 20.62 | 20.66 | 22.81 | 23.22 | 23.32 | 23.29 | 21.16 | 20.75 | 20.63
Outpatient | 90.1-2010 | ASHRAE 169-2013-3C | 20.59 | 20.59 | 20.58 | 20.65 | 20.69 | 21.58 | 21.79 | 21.85 | 21.81 | 20.95 | 20.73 | 20.64
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-3C | 20.77 | 20.76 | 20.74 | 20.78 | 20.8 | 23.01 | 23.35 | 23.43 | 23.43 | 21.21 | 20.9 | 20.82
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-3C | 20.38 | 20.38 | 20.36 | 20.49 | 20.56 | 22.77 | 23.18 | 23.28 | 23.21 | 21.05 | 20.61 | 20.46
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-3C | 20.78 | 20.77 | 20.75 | 20.79 | 20.81 | 23.01 | 23.36 | 23.43 | 23.44 | 21.22 | 20.91 | 20.83
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-3C | 20.72 | 20.71 | 20.69 | 20.74 | 20.77 | 22.98 | 23.33 | 23.41 | 23.4 | 21.19 | 20.87 | 20.77
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-3C | 20.83 | 20.82 | 20.8 | 20.83 | 20.84 | 23.05 | 23.38 | 23.45 | 23.46 | 21.24 | 20.95 | 20.87
SmallHotel | 90.1-2010 | ASHRAE 169-2013-3C | 20.54 | 20.55 | 20.54 | 20.62 | 20.67 | 20.73 | 20.82 | 20.85 | 20.8 | 20.78 | 20.65 | 20.58
SmallOffice | 90.1-2010 | ASHRAE 169-2013-3C | 20.36 | 20.34 | 20.32 | 20.42 | 20.5 | 22.45 | 23 | 23.16 | 23.14 | 21.22 | 20.69 | 20.48
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
Warehouse | 90.1-2010 | ASHRAE 169-2013-3C | 13.38 | 13.38 | 12.92 | 14.88 | 15.38 | 17.13 | 18.76 | 19.25 | 18.38 | 18.54 | 14.85 | 13.86
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3C | 20.56 | 20.56 | 20.54 | 20.63 | 20.67 | 22.88 | 23.26 | 23.35 | 23.31 | 21.13 | 20.75 | 20.63
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-3C | 20.67 | 20.66 | 20.63 | 20.67 | 20.7 | 22.85 | 23.24 | 23.33 | 23.34 | 21.19 | 20.85 | 20.74
Hospital | 90.1-2013 | ASHRAE 169-2013-3C | 20.8 | 20.78 | 20.77 | 20.79 | 20.81 | 22.96 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeHotel | 90.1-2013 | ASHRAE 169-2013-3C | 20.55 | 20.55 | 20.54 | 20.6 | 20.64 | 20.69 | 20.76 | 20.79 | 20.75 | 20.74 | 20.65 | 20.58
LargeOffice | 90.1-2013 | ASHRAE 169-2013-3C | 20.79 | 20.78 | 20.76 | 20.79 | 20.81 | 22.95 | 23.33 | 23.41 | 23.42 | 21.25 | 20.93 | 20.84
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3C
MediumOffice | 90.1-2013 | ASHRAE 169-2013-3C | 20.71 | 20.7 | 20.68 | 20.73 | 20.76 | 22.9 | 23.29 | 23.38 | 23.37 | 21.22 | 20.87 | 20.77
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-3C | 20.67 | 20.66 | 20.63 | 20.67 | 20.7 | 22.85 | 23.24 | 23.33 | 23.34 | 21.19 | 20.85 | 20.74
Outpatient | 90.1-2013 | ASHRAE 169-2013-3C | 20.59 | 20.59 | 20.58 | 20.65 | 20.69 | 21.58 | 21.79 | 21.85 | 21.81 | 20.95 | 20.73 | 20.64
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-3C | 20.77 | 20.76 | 20.74 | 20.78 | 20.8 | 23.01 | 23.35 | 23.43 | 23.43 | 21.21 | 20.9 | 20.82
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-3C | 20.38 | 20.38 | 20.36 | 20.49 | 20.56 | 22.77 | 23.18 | 23.28 | 23.21 | 21.05 | 20.61 | 20.46
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-3C | 20.78 | 20.77 | 20.75 | 20.79 | 20.81 | 23.01 | 23.36 | 23.43 | 23.44 | 21.22 | 20.91 | 20.83
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-3C | 20.72 | 20.71 | 20.69 | 20.74 | 20.77 | 22.98 | 23.33 | 23.41 | 23.4 | 21.19 | 20.87 | 20.77
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-3C | 20.83 | 20.82 | 20.8 | 20.83 | 20.84 | 23.05 | 23.38 | 23.45 | 23.46 | 21.24 | 20.95 | 20.87
SmallHotel | 90.1-2013 | ASHRAE 169-2013-3C | 20.54 | 20.55 | 20.54 | 20.62 | 20.67 | 20.73 | 20.82 | 20.85 | 20.8 | 20.78 | 20.65 | 20.58
SmallOffice | 90.1-2013 | ASHRAE 169-2013-3C | 20.36 | 20.34 | 20.32 | 20.42 | 20.5 | 22.45 | 23 | 23.16 | 23.14 | 21.22 | 20.69 | 20.48
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
Warehouse | 90.1-2013 | ASHRAE 169-2013-3C | 13.38 | 13.38 | 12.92 | 14.88 | 15.38 | 17.13 | 18.76 | 19.25 | 18.38 | 18.54 | 14.85 | 13.86
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4A | 20.03 | 19.93 | 20.06 | 20.25 | 20.45 | 22.86 | 23.31 | 23.44 | 23.37 | 21 | 20.49 | 20.22
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-4A | 20.02 | 19.92 | 20.05 | 20.23 | 20.43 | 22.78 | 23.27 | 23.4 | 23.34 | 21.02 | 20.49 | 20.21
Hospital | 90.1-2004 | ASHRAE 169-2013-4A | 20.57 | 20.52 | 20.56 | 20.63 | 20.71 | 22.94 | 23.35 | 23.44 | 23.44 | 21.2 | 20.82 | 20.67
LargeHotel | 90.1-2004 | ASHRAE 169-2013-4A | 20.16 | 20.09 | 20.18 | 20.3 | 20.45 | 20.64 | 20.77 | 20.84 | 20.79 | 20.65 | 20.46 | 20.28
LargeOffice | 90.1-2004 | ASHRAE 169-2013-4A | 20.56 | 20.5 | 20.55 | 20.62 | 20.7 | 22.94 | 23.34 | 23.44 | 23.44 | 21.19 | 20.81 | 20.66
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-4A | 20.37 | 20.3 | 20.38 | 20.49 | 20.61 | 22.88 | 23.32 | 23.43 | 23.4 | 21.13 | 20.7 | 20.5
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-4A | 20.02 | 19.92 | 20.05 | 20.23 | 20.43 | 22.78 | 23.27 | 23.4 | 23.34 | 21.02 | 20.49 | 20.21
Outpatient | 90.1-2004 | ASHRAE 169-2013-4A | 20.15 | 20.07 | 20.18 | 20.33 | 20.5 | 21.55 | 21.82 | 21.91 | 21.85 | 20.84 | 20.51 | 20.3
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-4A | 20.5 | 20.44 | 20.5 | 20.58 | 20.68 | 22.99 | 23.38 | 23.47 | 23.46 | 21.15 | 20.77 | 20.61
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4A | 19.6 | 19.46 | 19.67 | 19.94 | 20.24 | 22.74 | 23.26 | 23.42 | 23.3 | 20.86 | 20.24 | 19.86
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-4A | 20.52 | 20.46 | 20.52 | 20.6 | 20.7 | 23 | 23.38 | 23.47 | 23.46 | 21.15 | 20.79 | 20.63
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-4A | 20.39 | 20.32 | 20.39 | 20.5 | 20.63 | 22.96 | 23.36 | 23.46 | 23.43 | 21.11 | 20.71 | 20.51
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-4A | 20.64 | 20.59 | 20.63 | 20.69 | 20.76 | 23.03 | 23.4 | 23.48 | 23.48 | 21.19 | 20.86 | 20.72
SmallHotel | 90.1-2004 | ASHRAE 169-2013-4A | 20.06 | 19.98 | 20.1 | 20.27 | 20.46 | 20.7 | 20.85 | 20.91 | 20.84 | 20.66 | 20.41 | 20.2
SmallOffice | 90.1-2004 | ASHRAE 169-2013-4A | 19.62 | 19.46 | 19.6 | 19.84 | 20.13 | 22.36 | 23.04 | 23.27 | 23.23 | 21.07 | 20.35 | 19.92
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
Warehouse | 90.1-2004 | ASHRAE 169-2013-4A | 12.76 | 12.67 | 12.69 | 12.73 | 15.42 | 20.26 | 23.61 | 23.99 | 20.15 | 14.85 | 13.2 | 12.9
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4A | 20.03 | 19.93 | 20.06 | 20.25 | 20.45 | 22.86 | 23.31 | 23.44 | 23.37 | 21 | 20.49 | 20.22
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-4A | 20.33 | 20.24 | 20.28 | 20.37 | 20.49 | 22.77 | 23.22 | 23.35 | 23.37 | 21.12 | 20.7 | 20.48
Hospital | 90.1-2007 | ASHRAE 169-2013-4A | 20.57 | 20.52 | 20.56 | 20.63 | 20.71 | 22.94 | 23.35 | 23.44 | 23.44 | 21.2 | 20.82 | 20.67
LargeHotel | 90.1-2007 | ASHRAE 169-2013-4A | 20.16 | 20.09 | 20.18 | 20.3 | 20.45 | 20.64 | 20.77 | 20.84 | 20.79 | 20.65 | 20.46 | 20.28
LargeOffice | 90.1-2007 | ASHRAE 169-2013-4A | 20.56 | 20.5 | 20.55 | 20.62 | 20.7 | 22.94 | 23.34 | 23.44 | 23.44 | 21.19 | 20.81 | 20.66
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-4A | 20.37 | 20.3 | 20.38 | 20.49 | 20.61 | 22.88 | 23.32 | 23.43 | 23.4 | 21.13 | 20.7 | 20.5
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-4A | 20.33 | 20.24 | 20.28 | 20.37 | 20.49 | 22.77 | 23.22 | 23.35 | 23.37 | 21.12 | 20.7 | 20.48
Outpatient | 90.1-2007 | ASHRAE 169-2013-4A | 20.15 | 20.07 | 20.18 | 20.33 | 20.5 | 21.55 | 21.82 | 21.91 | 21.85 | 20.84 | 20.51 | 20.3
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-4A | 20.5 | 20.44 | 20.5 | 20.58 | 20.68 | 22.99 | 23.38 | 23.47 | 23.46 | 21.15 | 20.77 | 20.61
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4A | 19.6 | 19.46 | 19.67 | 19.94 | 20.24 | 22.74 | 23.26 | 23.42 | 23.3 | 20.86 | 20.24 | 19.86
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-4A | 20.52 | 20.46 | 20.52 | 20.6 | 20.7 | 23 | 23.38 | 23.47 | 23.46 | 21.15 | 20.79 | 20.63
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-4A | 20.39 | 20.32 | 20.39 | 20.5 | 20.63 | 22.96 | 23.36 | 23.46 | 23.43 | 21.11 | 20.71 | 20.51
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-4A | 20.64 | 20.59 | 20.63 | 20.69 | 20.76 | 23.03 | 23.4 | 23.48 | 23.48 | 21.19 | 20.86 | 20.72
SmallHotel | 90.1-2007 | ASHRAE 169-2013-4A | 20.06 | 19.98 | 20.1 | 20.27 | 20.46 | 20.7 | 20.85 | 20.91 | 20.84 | 20.66 | 20.41 | 20.2
SmallOffice | 90.1-2007 | ASHRAE 169-2013-4A | 19.62 | 19.46 | 19.6 | 19.84 | 20.13 | 22.36 | 23.04 | 23.27 | 23.23 | 21.07 | 20.35 | 19.92
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
Warehouse | 90.1-2007 | ASHRAE 169-2013-4A | 12.76 | 12.67 | 12.69 | 12.73 | 15.42 | 20.26 | 23.61 | 23.99 | 20.15 | 14.85 | 13.2 | 12.9
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4A | 20.03 | 19.93 | 20.06 | 20.25 | 20.45 | 22.86 | 23.31 | 23.44 | 23.37 | 21 | 20.49 | 20.22
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-4A | 20.33 | 20.24 | 20.28 | 20.37 | 20.49 | 22.77 | 23.22 | 23.35 | 23.37 | 21.12 | 20.7 | 20.48
Hospital | 90.1-2010 | ASHRAE 169-2013-4A | 20.57 | 20.52 | 20.56 | 20.63 | 20.71 | 22.94 | 23.35 | 23.44 | 23.44 | 21.2 | 20.82 | 20.67
LargeHotel | 90.1-2010 | ASHRAE 169-2013-4A | 20.16 | 20.09 | 20.18 | 20.3 | 20.45 | 20.64 | 20.77 | 20.84 | 20.79 | 20.65 | 20.46 | 20.28
LargeOffice | 90.1-2010 | ASHRAE 169-2013-4A | 20.56 | 20.5 | 20.55 | 20.62 | 20.7 | 22.94 | 23.34 | 23.44 | 23.44 | 21.19 | 20.81 | 20.66
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-4A | 20.37 | 20.3 | 20.38 | 20.49 | 20.61 | 22.88 | 23.32 | 23.43 | 23.4 | 21.13 | 20.7 | 20.5
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-4A | 20.33 | 20.24 | 20.28 | 20.37 | 20.49 | 22.77 | 23.22 | 23.35 | 23.37 | 21.12 | 20.7 | 20.48
Outpatient | 90.1-2010 | ASHRAE 169-2013-4A | 20.15 | 20.07 | 20.18 | 20.33 | 20.5 | 21.55 | 21.82 | 21.91 | 21.85 | 20.84 | 20.51 | 20.3
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-4A | 20.5 | 20.44 | 20.5 | 20.58 | 20.68 | 22.99 | 23.38 | 23.47 | 23.46 | 21.15 | 20.77 | 20.61
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4A | 19.6 | 19.46 | 19.67 | 19.94 | 20.24 | 22.74 | 23.26 | 23.42 | 23.3 | 20.86 | 20.24 | 19.86
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-4A | 20.52 | 20.46 | 20.52 | 20.6 | 20.7 | 23 | 23.38 | 23.47 | 23.46 | 21.15 | 20.79 | 20.63
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-4A | 20.39 | 20.32 | 20.39 | 20.5 | 20.63 | 22.96 | 23.36 | 23.46 | 23.43 | 21.11 | 20.71 | 20.51
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-4A | 20.64 | 20.59 | 20.63 | 20.69 | 20.76 | 23.03 | 23.4 | 23.48 | 23.48 | 21.19 | 20.86 | 20.72
SmallHotel | 90.1-2010 | ASHRAE 169-2013-4A | 20.06 | 19.98 | 20.1 | 20.27 | 20.46 | 20.7 | 20.85 | 20.91 | 20.84 | 20.66 | 20.41 | 20.2
SmallOffice | 90.1-2010 | ASHRAE 169-2013-4A | 19.62 | 19.46 | 19.6 | 19.84 | 20.13 | 22.36 | 23.04 | 23.27 | 23.23 | 21.07 | 20.35 | 19.92
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
Warehouse | 90.1-2010 | ASHRAE 169-2013-4A | 12.76 | 12.67 | 12.69 | 12.73 | 15.42 | 20.26 | 23.61 | 23.99 | 20.15 | 14.85 | 13.2 | 12.9
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4A | 20.49 | 20.41 | 20.42 | 20.47 | 20.55 | 22.86 | 23.26 | 23.38 | 23.41 | 21.13 | 20.78 | 20.62
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-4A | 20.39 | 20.3 | 20.32 | 20.39 | 20.5 | 22.77 | 23.22 | 23.35 | 23.37 | 21.13 | 20.73 | 20.53
Hospital | 90.1-2013 | ASHRAE 169-2013-4A | 20.72 | 20.67 | 20.67 | 20.7 | 20.74 | 22.94 | 23.33 | 23.42 | 23.45 | 21.24 | 20.92 | 20.8
LargeHotel | 90.1-2013 | ASHRAE 169-2013-4A | 20.39 | 20.33 | 20.35 | 20.41 | 20.49 | 20.61 | 20.71 | 20.78 | 20.78 | 20.71 | 20.61 | 20.49
LargeOffice | 90.1-2013 | ASHRAE 169-2013-4A | 20.71 | 20.66 | 20.66 | 20.69 | 20.73 | 22.93 | 23.32 | 23.42 | 23.45 | 21.24 | 20.91 | 20.79
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-4A | 20.6 | 20.54 | 20.54 | 20.59 | 20.65 | 22.88 | 23.28 | 23.39 | 23.42 | 21.2 | 20.85 | 20.7
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4A | 20.58 | 20.52 | 20.55 | 20.59 | 20.67 | 22.89 | 23.29 | 23.4 | 23.42 | 21.21 | 20.85 | 20.69
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-4A | 20.39 | 20.3 | 20.32 | 20.39 | 20.5 | 22.77 | 23.22 | 23.35 | 23.37 | 21.13 | 20.73 | 20.53
Outpatient | 90.1-2013 | ASHRAE 169-2013-4A | 20.46 | 20.39 | 20.41 | 20.47 | 20.56 | 21.53 | 21.76 | 21.85 | 21.86 | 20.93 | 20.71 | 20.56
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-4A | 20.72 | 20.67 | 20.67 | 20.7 | 20.74 | 23 | 23.35 | 23.44 | 23.48 | 21.21 | 20.91 | 20.8
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4A | 20.29 | 20.18 | 20.19 | 20.27 | 20.39 | 22.75 | 23.18 | 23.33 | 23.36 | 21.06 | 20.67 | 20.45
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-4A | 20.74 | 20.69 | 20.69 | 20.71 | 20.75 | 23 | 23.36 | 23.45 | 23.48 | 21.22 | 20.92 | 20.81
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-4A | 20.67 | 20.61 | 20.61 | 20.64 | 20.69 | 22.96 | 23.33 | 23.43 | 23.46 | 21.19 | 20.88 | 20.76
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-4A | 20.8 | 20.76 | 20.75 | 20.77 | 20.79 | 23.04 | 23.38 | 23.46 | 23.5 | 21.24 | 20.96 | 20.86
SmallHotel | 90.1-2013 | ASHRAE 169-2013-4A | 20.39 | 20.32 | 20.35 | 20.42 | 20.52 | 20.66 | 20.77 | 20.84 | 20.83 | 20.75 | 20.63 | 20.49
SmallOffice | 90.1-2013 | ASHRAE 169-2013-4A | 20.14 | 20 | 20 | 20.1 | 20.24 | 22.35 | 22.97 | 23.19 | 23.25 | 21.21 | 20.67 | 20.37
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4A | 20.11 | 19.97 | 20.01 | 20.1 | 20.27 | 22.38 | 22.99 | 23.2 | 23.25 | 21.22 | 20.67 | 20.35
Warehouse | 90.1-2013 | ASHRAE 169-2013-4A | 12.76 | 12.67 | 12.69 | 12.73 | 15.42 | 20.26 | 23.61 | 23.99 | 20.15 | 14.85 | 13.2 | 12.9
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4B | 20.16 | 20.14 | 20.27 | 20.45 | 20.64 | 23.01 | 23.47 | 23.55 | 23.48 | 21.09 | 20.56 | 20.26
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-4B | 20.15 | 20.13 | 20.25 | 20.43 | 20.63 | 22.93 | 23.43 | 23.51 | 23.44 | 21.12 | 20.56 | 20.25
Hospital | 90.1-2004 | ASHRAE 169-2013-4B | 20.63 | 20.61 | 20.65 | 20.72 | 20.79 | 23.01 | 23.41 | 23.49 | 23.48 | 21.24 | 20.85 | 20.69
LargeHotel | 90.1-2004 | ASHRAE 169-2013-4B | 20.25 | 20.24 | 20.33 | 20.46 | 20.6 | 20.76 | 20.89 | 20.93 | 20.87 | 20.73 | 20.51 | 20.32
LargeOffice | 90.1-2004 | ASHRAE 169-2013-4B | 20.61 | 20.6 | 20.64 | 20.71 | 20.79 | 23 | 23.41 | 23.49 | 23.48 | 21.24 | 20.84 | 20.68
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4B
MediumOffice | 90.1-2004 | ASHRAE 169-2013-4B | 20.45 | 20.44 | 20.51 | 20.61 | 20.73 | 22.98 | 23.42 | 23.5 | 23.47 | 21.2 | 20.74 | 20.53
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-4B | 20.15 | 20.13 | 20.25 | 20.43 | 20.63 | 22.93 | 23.43 | 23.51 | 23.44 | 21.12 | 20.56 | 20.25
Outpatient | 90.1-2004 | ASHRAE 169-2013-4B | 20.26 | 20.25 | 20.35 | 20.5 | 20.66 | 21.68 | 21.95 | 22 | 21.93 | 20.93 | 20.56 | 20.33
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-4B | 20.56 | 20.55 | 20.6 | 20.69 | 20.78 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4B | 19.78 | 19.77 | 19.96 | 20.23 | 20.52 | 22.96 | 23.49 | 23.58 | 23.45 | 21 | 20.33 | 19.91
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-4B | 20.58 | 20.57 | 20.62 | 20.7 | 20.79 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.82 | 20.65
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-4B | 20.47 | 20.45 | 20.52 | 20.63 | 20.75 | 23.05 | 23.46 | 23.53 | 23.5 | 21.17 | 20.74 | 20.54
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-4B | 20.68 | 20.67 | 20.7 | 20.76 | 20.83 | 23.09 | 23.46 | 23.53 | 23.52 | 21.23 | 20.88 | 20.74
SmallHotel | 90.1-2004 | ASHRAE 169-2013-4B | 20.17 | 20.17 | 20.29 | 20.46 | 20.64 | 20.83 | 20.99 | 21.01 | 20.93 | 20.75 | 20.47 | 20.24
SmallOffice | 90.1-2004 | ASHRAE 169-2013-4B | 19.78 | 19.72 | 19.87 | 20.12 | 20.4 | 22.57 | 23.26 | 23.42 | 23.36 | 21.2 | 20.43 | 19.98
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
Warehouse | 90.1-2004 | ASHRAE 169-2013-4B | 12.81 | 12.75 | 12.77 | 13.7 | 16.95 | 21.71 | 24.35 | 23.6 | 20.67 | 14.7 | 13.22 | 12.92
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4B | 20.16 | 20.14 | 20.27 | 20.45 | 20.64 | 23.01 | 23.47 | 23.55 | 23.48 | 21.09 | 20.56 | 20.26
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-4B | 20.41 | 20.37 | 20.42 | 20.51 | 20.63 | 22.88 | 23.35 | 23.45 | 23.45 | 21.2 | 20.75 | 20.52
Hospital | 90.1-2007 | ASHRAE 169-2013-4B | 20.63 | 20.61 | 20.65 | 20.72 | 20.79 | 23.01 | 23.41 | 23.49 | 23.48 | 21.24 | 20.85 | 20.69
LargeHotel | 90.1-2007 | ASHRAE 169-2013-4B | 20.25 | 20.24 | 20.33 | 20.46 | 20.6 | 20.76 | 20.89 | 20.93 | 20.87 | 20.73 | 20.51 | 20.32
LargeOffice | 90.1-2007 | ASHRAE 169-2013-4B | 20.61 | 20.6 | 20.64 | 20.71 | 20.79 | 23 | 23.41 | 23.49 | 23.48 | 21.24 | 20.84 | 20.68
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4B
MediumOffice | 90.1-2007 | ASHRAE 169-2013-4B | 20.45 | 20.44 | 20.51 | 20.61 | 20.73 | 22.98 | 23.42 | 23.5 | 23.47 | 21.2 | 20.74 | 20.53
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-4B | 20.41 | 20.37 | 20.42 | 20.51 | 20.63 | 22.88 | 23.35 | 23.45 | 23.45 | 21.2 | 20.75 | 20.52
Outpatient | 90.1-2007 | ASHRAE 169-2013-4B | 20.26 | 20.25 | 20.35 | 20.5 | 20.66 | 21.68 | 21.95 | 22 | 21.93 | 20.93 | 20.56 | 20.33
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-4B | 20.56 | 20.55 | 20.6 | 20.69 | 20.78 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4B | 19.78 | 19.77 | 19.96 | 20.23 | 20.52 | 22.96 | 23.49 | 23.58 | 23.45 | 21 | 20.33 | 19.91
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-4B | 20.58 | 20.57 | 20.62 | 20.7 | 20.79 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.82 | 20.65
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-4B | 20.47 | 20.45 | 20.52 | 20.63 | 20.75 | 23.05 | 23.46 | 23.53 | 23.5 | 21.17 | 20.74 | 20.54
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-4B | 20.68 | 20.67 | 20.7 | 20.76 | 20.83 | 23.09 | 23.46 | 23.53 | 23.52 | 21.23 | 20.88 | 20.74
SmallHotel | 90.1-2007 | ASHRAE 169-2013-4B | 20.17 | 20.17 | 20.29 | 20.46 | 20.64 | 20.83 | 20.99 | 21.01 | 20.93 | 20.75 | 20.47 | 20.24
SmallOffice | 90.1-2007 | ASHRAE 169-2013-4B | 19.78 | 19.72 | 19.87 | 20.12 | 20.4 | 22.57 | 23.26 | 23.42 | 23.36 | 21.2 | 20.43 | 19.98
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
Warehouse | 90.1-2007 | ASHRAE 169-2013-4B | 12.81 | 12.75 | 12.77 | 13.7 | 16.95 | 21.71 | 24.35 | 23.6 | 20.67 | 14.7 | 13.22 | 12.92
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4B | 20.16 | 20.14 | 20.27 | 20.45 | 20.64 | 23.01 | 23.47 | 23.55 | 23.48 | 21.09 | 20.56 | 20.26
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-4B | 20.41 | 20.37 | 20.42 | 20.51 | 20.63 | 22.88 | 23.35 | 23.45 | 23.45 | 21.2 | 20.75 | 20.52
Hospital | 90.1-2010 | ASHRAE 169-2013-4B | 20.63 | 20.61 | 20.65 | 20.72 | 20.79 | 23.01 | 23.41 | 23.49 | 23.48 | 21.24 | 20.85 | 20.69
LargeHotel | 90.1-2010 | ASHRAE 169-2013-4B | 20.25 | 20.24 | 20.33 | 20.46 | 20.6 | 20.76 | 20.89 | 20.93 | 20.87 | 20.73 | 20.51 | 20.32
LargeOffice | 90.1-2010 | ASHRAE 169-2013-4B | 20.61 | 20.6 | 20.64 | 20.71 | 20.79 | 23 | 23.41 | 23.49 | 23.48 | 21.24 | 20.84 | 20.68
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4B
MediumOffice | 90.1-2010 | ASHRAE 169-2013-4B | 20.45 | 20.44 | 20.51 | 20.61 | 20.73 | 22.98 | 23.42 | 23.5 | 23.47 | 21.2 | 20.74 | 20.53
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-4B | 20.41 | 20.37 | 20.42 | 20.51 | 20.63 | 22.88 | 23.35 | 23.45 | 23.45 | 21.2 | 20.75 | 20.52
Outpatient | 90.1-2010 | ASHRAE 169-2013-4B | 20.26 | 20.25 | 20.35 | 20.5 | 20.66 | 21.68 | 21.95 | 22 | 21.93 | 20.93 | 20.56 | 20.33
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-4B | 20.56 | 20.55 | 20.6 | 20.69 | 20.78 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4B | 19.78 | 19.77 | 19.96 | 20.23 | 20.52 | 22.96 | 23.49 | 23.58 | 23.45 | 21 | 20.33 | 19.91
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-4B | 20.58 | 20.57 | 20.62 | 20.7 | 20.79 | 23.07 | 23.46 | 23.53 | 23.51 | 21.2 | 20.82 | 20.65
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-4B | 20.47 | 20.45 | 20.52 | 20.63 | 20.75 | 23.05 | 23.46 | 23.53 | 23.5 | 21.17 | 20.74 | 20.54
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-4B | 20.68 | 20.67 | 20.7 | 20.76 | 20.83 | 23.09 | 23.46 | 23.53 | 23.52 | 21.23 | 20.88 | 20.74
SmallHotel | 90.1-2010 | ASHRAE 169-2013-4B | 20.17 | 20.17 | 20.29 | 20.46 | 20.64 | 20.83 | 20.99 | 21.01 | 20.93 | 20.75 | 20.47 | 20.24
SmallOffice | 90.1-2010 | ASHRAE 169-2013-4B | 19.78 | 19.72 | 19.87 | 20.12 | 20.4 | 22.57 | 23.26 | 23.42 | 23.36 | 21.2 | 20.43 | 19.98
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
Warehouse | 90.1-2010 | ASHRAE 169-2013-4B | 12.81 | 12.75 | 12.77 | 13.7 | 16.95 | 21.71 | 24.35 | 23.6 | 20.67 | 14.7 | 13.22 | 12.92
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4B | 20.55 | 20.5 | 20.52 | 20.58 | 20.67 | 22.96 | 23.36 | 23.47 | 23.48 | 21.2 | 20.83 | 20.65
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-4B | 20.46 | 20.41 | 20.44 | 20.52 | 20.63 | 22.88 | 23.33 | 23.45 | 23.45 | 21.21 | 20.78 | 20.57
Hospital | 90.1-2013 | ASHRAE 169-2013-4B | 20.75 | 20.72 | 20.73 | 20.75 | 20.8 | 22.99 | 23.38 | 23.46 | 23.49 | 21.28 | 20.94 | 20.82
LargeHotel | 90.1-2013 | ASHRAE 169-2013-4B | 20.45 | 20.42 | 20.45 | 20.51 | 20.6 | 20.7 | 20.81 | 20.86 | 20.85 | 20.79 | 20.65 | 20.52
LargeOffice | 90.1-2013 | ASHRAE 169-2013-4B | 20.75 | 20.71 | 20.72 | 20.75 | 20.79 | 22.98 | 23.37 | 23.46 | 23.49 | 21.28 | 20.93 | 20.81
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4B
MediumOffice | 90.1-2013 | ASHRAE 169-2013-4B | 20.65 | 20.61 | 20.62 | 20.67 | 20.74 | 22.95 | 23.36 | 23.46 | 23.47 | 21.25 | 20.88 | 20.73
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4B | 20.63 | 20.6 | 20.61 | 20.65 | 20.73 | 22.95 | 23.35 | 23.45 | 23.47 | 21.25 | 20.88 | 20.73
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-4B | 20.46 | 20.41 | 20.44 | 20.52 | 20.63 | 22.88 | 23.33 | 23.45 | 23.45 | 21.21 | 20.78 | 20.57
Outpatient | 90.1-2013 | ASHRAE 169-2013-4B | 20.52 | 20.48 | 20.51 | 20.58 | 20.67 | 21.62 | 21.86 | 21.93 | 21.92 | 21 | 20.75 | 20.6
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-4B | 20.76 | 20.72 | 20.73 | 20.75 | 20.8 | 23.05 | 23.41 | 23.49 | 23.52 | 21.25 | 20.94 | 20.82
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4B | 20.37 | 20.3 | 20.34 | 20.43 | 20.56 | 22.89 | 23.33 | 23.46 | 23.46 | 21.16 | 20.74 | 20.5
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-4B | 20.77 | 20.74 | 20.74 | 20.76 | 20.8 | 23.05 | 23.41 | 23.49 | 23.52 | 21.25 | 20.95 | 20.83
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-4B | 20.71 | 20.67 | 20.68 | 20.71 | 20.76 | 23.03 | 23.4 | 23.48 | 23.51 | 21.24 | 20.91 | 20.78
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-4B | 20.82 | 20.79 | 20.79 | 20.81 | 20.84 | 23.07 | 23.42 | 23.5 | 23.53 | 21.26 | 20.97 | 20.88
SmallHotel | 90.1-2013 | ASHRAE 169-2013-4B | 20.45 | 20.42 | 20.46 | 20.54 | 20.64 | 20.76 | 20.88 | 20.92 | 20.9 | 20.83 | 20.67 | 20.53
SmallOffice | 90.1-2013 | ASHRAE 169-2013-4B | 20.23 | 20.13 | 20.16 | 20.27 | 20.43 | 22.51 | 23.12 | 23.32 | 23.35 | 21.31 | 20.74 | 20.42
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4B | 20.19 | 20.12 | 20.14 | 20.23 | 20.41 | 22.51 | 23.11 | 23.3 | 23.34 | 21.3 | 20.73 | 20.41
Warehouse | 90.1-2013 | ASHRAE 169-2013-4B | 12.81 | 12.75 | 12.77 | 13.7 | 16.95 | 21.71 | 24.35 | 23.6 | 20.67 | 14.7 | 13.22 | 12.92
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4C | 20.08 | 20.08 | 20.18 | 20.27 | 20.41 | 22.67 | 23.06 | 23.2 | 23.13 | 20.81 | 20.4 | 20.19
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-4C | 20.08 | 20.07 | 20.16 | 20.26 | 20.39 | 22.59 | 23.02 | 23.16 | 23.1 | 20.83 | 20.4 | 20.19
Hospital | 90.1-2004 | ASHRAE 169-2013-4C | 20.6 | 20.58 | 20.61 | 20.64 | 20.7 | 22.86 | 23.24 | 23.34 | 23.34 | 21.12 | 20.78 | 20.66
LargeHotel | 90.1-2004 | ASHRAE 169-2013-4C | 20.18 | 20.18 | 20.25 | 20.32 | 20.43 | 20.51 | 20.6 | 20.66 | 20.61 | 20.49 | 20.37 | 20.25
LargeOffice | 90.1-2004 | ASHRAE 169-2013-4C | 20.58 | 20.57 | 20.6 | 20.63 | 20.69 | 22.86 | 23.24 | 23.34 | 23.34 | 21.11 | 20.77 | 20.65
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4C
MediumOffice | 90.1-2004 | ASHRAE 169-2013-4C | 20.41 | 20.39 | 20.45 | 20.5 | 20.59 | 22.76 | 23.16 | 23.27 | 23.25 | 21.01 | 20.64 | 20.49
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-4C | 20.08 | 20.07 | 20.16 | 20.26 | 20.39 | 22.59 | 23.02 | 23.16 | 23.1 | 20.83 | 20.4 | 20.19
Outpatient | 90.1-2004 | ASHRAE 169-2013-4C | 20.2 | 20.19 | 20.28 | 20.36 | 20.47 | 21.4 | 21.62 | 21.71 | 21.66 | 20.68 | 20.43 | 20.28
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-4C | 20.52 | 20.51 | 20.55 | 20.6 | 20.66 | 22.9 | 23.25 | 23.35 | 23.34 | 21.05 | 20.72 | 20.59
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-4C | 19.68 | 19.68 | 19.83 | 19.98 | 20.19 | 22.46 | 22.9 | 23.06 | 22.95 | 20.58 | 20.1 | 19.83
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-4C | 20.55 | 20.53 | 20.57 | 20.61 | 20.68 | 22.91 | 23.26 | 23.36 | 23.35 | 21.06 | 20.74 | 20.61
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-4C | 20.42 | 20.41 | 20.46 | 20.52 | 20.6 | 22.84 | 23.2 | 23.31 | 23.29 | 20.99 | 20.64 | 20.5
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-4C | 20.65 | 20.64 | 20.67 | 20.7 | 20.74 | 22.97 | 23.31 | 23.4 | 23.4 | 21.12 | 20.82 | 20.71
SmallHotel | 90.1-2004 | ASHRAE 169-2013-4C | 20.1 | 20.11 | 20.21 | 20.3 | 20.43 | 20.53 | 20.63 | 20.71 | 20.63 | 20.48 | 20.33 | 20.18
SmallOffice | 90.1-2004 | ASHRAE 169-2013-4C | 19.7 | 19.66 | 19.77 | 19.9 | 20.1 | 22.13 | 22.7 | 22.92 | 22.88 | 20.79 | 20.2 | 19.88
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
Warehouse | 90.1-2004 | ASHRAE 169-2013-4C | 12.65 | 12.64 | 12.66 | 12.69 | 12.91 | 15.02 | 17 | 18.18 | 15.36 | 13.12 | 12.83 | 12.72
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4C | 20.08 | 20.08 | 20.18 | 20.27 | 20.41 | 22.67 | 23.06 | 23.2 | 23.13 | 20.81 | 20.4 | 20.19
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-4C | 20.33 | 20.3 | 20.34 | 20.39 | 20.48 | 22.66 | 23.07 | 23.19 | 23.2 | 20.97 | 20.6 | 20.44
Hospital | 90.1-2007 | ASHRAE 169-2013-4C | 20.6 | 20.58 | 20.61 | 20.64 | 20.7 | 22.86 | 23.24 | 23.34 | 23.34 | 21.12 | 20.78 | 20.66
LargeHotel | 90.1-2007 | ASHRAE 169-2013-4C | 20.18 | 20.18 | 20.25 | 20.32 | 20.43 | 20.51 | 20.6 | 20.66 | 20.61 | 20.49 | 20.37 | 20.25
LargeOffice | 90.1-2007 | ASHRAE 169-2013-4C | 20.58 | 20.57 | 20.6 | 20.63 | 20.69 | 22.86 | 23.24 | 23.34 | 23.34 | 21.11 | 20.77 | 20.65
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4C
MediumOffice | 90.1-2007 | ASHRAE 169-2013-4C | 20.41 | 20.39 | 20.45 | 20.5 | 20.59 | 22.76 | 23.16 | 23.27 | 23.25 | 21.01 | 20.64 | 20.49
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-4C | 20.33 | 20.3 | 20.34 | 20.39 | 20.48 | 22.66 | 23.07 | 23.19 | 23.2 | 20.97 | 20.6 | 20.44
Outpatient | 90.1-2007 | ASHRAE 169-2013-4C | 20.2 | 20.19 | 20.28 | 20.36 | 20.47 | 21.4 | 21.62 | 21.71 | 21.66 | 20.68 | 20.43 | 20.28
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-4C | 20.52 | 20.51 | 20.55 | 20.6 | 20.66 | 22.9 | 23.25 | 23.35 | 23.34 | 21.05 | 20.72 | 20.59
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-4C | 19.68 | 19.68 | 19.83 | 19.98 | 20.19 | 22.46 | 22.9 | 23.06 | 22.95 | 20.58 | 20.1 | 19.83
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-4C | 20.55 | 20.53 | 20.57 | 20.61 | 20.68 | 22.91 | 23.26 | 23.36 | 23.35 | 21.06 | 20.74 | 20.61
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-4C | 20.42 | 20.41 | 20.46 | 20.52 | 20.6 | 22.84 | 23.2 | 23.31 | 23.29 | 20.99 | 20.64 | 20.5
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-4C | 20.65 | 20.64 | 20.67 | 20.7 | 20.74 | 22.97 | 23.31 | 23.4 | 23.4 | 21.12 | 20.82 | 20.71
SmallHotel | 90.1-2007 | ASHRAE 169-2013-4C | 20.1 | 20.11 | 20.21 | 20.3 | 20.43 | 20.53 | 20.63 | 20.71 | 20.63 | 20.48 | 20.33 | 20.18
SmallOffice | 90.1-2007 | ASHRAE 169-2013-4C | 19.7 | 19.66 | 19.77 | 19.9 | 20.1 | 22.13 | 22.7 | 22.92 | 22.88 | 20.79 | 20.2 | 19.88
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
Warehouse | 90.1-2007 | ASHRAE 169-2013-4C | 12.65 | 12.64 | 12.66 | 12.69 | 12.91 | 15.02 | 17 | 18.18 | 15.36 | 13.12 | 12.83 | 12.72
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4C | 20.08 | 20.08 | 20.18 | 20.27 | 20.41 | 22.67 | 23.06 | 23.2 | 23.13 | 20.81 | 20.4 | 20.19
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-4C | 20.33 | 20.3 | 20.34 | 20.39 | 20.48 | 22.66 | 23.07 | 23.19 | 23.2 | 20.97 | 20.6 | 20.44
Hospital | 90.1-2010 | ASHRAE 169-2013-4C | 20.6 | 20.58 | 20.61 | 20.64 | 20.7 | 22.86 | 23.24 | 23.34 | 23.34 | 21.12 | 20.78 | 20.66
LargeHotel | 90.1-2010 | ASHRAE 169-2013-4C | 20.18 | 20.18 | 20.25 | 20.32 | 20.43 | 20.51 | 20.6 | 20.66 | 20.61 | 20.49 | 20.37 | 20.25
LargeOffice | 90.1-2010 | ASHRAE 169-2013-4C | 20.58 | 20.57 | 20.6 | 20.63 | 20.69 | 22.86 | 23.24 | 23.34 | 23.34 | 21.11 | 20.77 | 20.65
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4C
MediumOffice | 90.1-2010 | ASHRAE 169-2013-4C | 20.41 | 20.39 | 20.45 | 20.5 | 20.59 | 22.76 | 23.16 | 23.27 | 23.25 | 21.01 | 20.64 | 20.49
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-4C | 20.33 | 20.3 | 20.34 | 20.39 | 20.48 | 22.66 | 23.07 | 23.19 | 23.2 | 20.97 | 20.6 | 20.44
Outpatient | 90.1-2010 | ASHRAE 169-2013-4C | 20.2 | 20.19 | 20.28 | 20.36 | 20.47 | 21.4 | 21.62 | 21.71 | 21.66 | 20.68 | 20.43 | 20.28
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-4C | 20.52 | 20.51 | 20.55 | 20.6 | 20.66 | 22.9 | 23.25 | 23.35 | 23.34 | 21.05 | 20.72 | 20.59
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-4C | 19.68 | 19.68 | 19.83 | 19.98 | 20.19 | 22.46 | 22.9 | 23.06 | 22.95 | 20.58 | 20.1 | 19.83
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-4C | 20.55 | 20.53 | 20.57 | 20.61 | 20.68 | 22.91 | 23.26 | 23.36 | 23.35 | 21.06 | 20.74 | 20.61
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-4C | 20.42 | 20.41 | 20.46 | 20.52 | 20.6 | 22.84 | 23.2 | 23.31 | 23.29 | 20.99 | 20.64 | 20.5
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-4C | 20.65 | 20.64 | 20.67 | 20.7 | 20.74 | 22.97 | 23.31 | 23.4 | 23.4 | 21.12 | 20.82 | 20.71
SmallHotel | 90.1-2010 | ASHRAE 169-2013-4C | 20.1 | 20.11 | 20.21 | 20.3 | 20.43 | 20.53 | 20.63 | 20.71 | 20.63 | 20.48 | 20.33 | 20.18
SmallOffice | 90.1-2010 | ASHRAE 169-2013-4C | 19.7 | 19.66 | 19.77 | 19.9 | 20.1 | 22.13 | 22.7 | 22.92 | 22.88 | 20.79 | 20.2 | 19.88
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
Warehouse | 90.1-2010 | ASHRAE 169-2013-4C | 12.65 | 12.64 | 12.66 | 12.69 | 12.91 | 15.02 | 17 | 18.18 | 15.36 | 13.12 | 12.83 | 12.72
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4C | 20.47 | 20.44 | 20.46 | 20.49 | 20.55 | 22.79 | 23.15 | 23.26 | 23.28 | 21.01 | 20.69 | 20.56
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-4C | 20.38 | 20.34 | 20.37 | 20.42 | 20.49 | 22.68 | 23.08 | 23.2 | 23.22 | 21 | 20.63 | 20.48
Hospital | 90.1-2013 | ASHRAE 169-2013-4C | 20.72 | 20.69 | 20.7 | 20.71 | 20.74 | 22.9 | 23.27 | 23.36 | 23.39 | 21.19 | 20.87 | 20.78
LargeHotel | 90.1-2013 | ASHRAE 169-2013-4C | 20.38 | 20.36 | 20.39 | 20.42 | 20.49 | 20.54 | 20.6 | 20.66 | 20.65 | 20.6 | 20.52 | 20.44
LargeOffice | 90.1-2013 | ASHRAE 169-2013-4C | 20.71 | 20.68 | 20.69 | 20.7 | 20.73 | 22.89 | 23.26 | 23.35 | 23.38 | 21.18 | 20.87 | 20.77
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4C
MediumOffice | 90.1-2013 | ASHRAE 169-2013-4C | 20.59 | 20.56 | 20.58 | 20.6 | 20.65 | 22.82 | 23.2 | 23.3 | 23.32 | 21.12 | 20.79 | 20.67
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4C | 20.59 | 20.57 | 20.57 | 20.58 | 20.63 | 22.82 | 23.2 | 23.31 | 23.34 | 21.13 | 20.78 | 20.67
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-4C | 20.38 | 20.34 | 20.37 | 20.42 | 20.49 | 22.68 | 23.08 | 23.2 | 23.22 | 21 | 20.63 | 20.48
Outpatient | 90.1-2013 | ASHRAE 169-2013-4C | 20.45 | 20.43 | 20.45 | 20.49 | 20.56 | 21.46 | 21.65 | 21.73 | 21.73 | 20.82 | 20.62 | 20.52
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-4C | 20.72 | 20.69 | 20.69 | 20.7 | 20.73 | 22.96 | 23.29 | 23.38 | 23.41 | 21.15 | 20.87 | 20.77
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-4C | 20.26 | 20.22 | 20.25 | 20.3 | 20.39 | 22.65 | 23.02 | 23.15 | 23.17 | 20.89 | 20.54 | 20.37
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-4C | 20.73 | 20.7 | 20.71 | 20.72 | 20.74 | 22.97 | 23.3 | 23.39 | 23.41 | 21.16 | 20.88 | 20.79
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-4C | 20.66 | 20.63 | 20.63 | 20.65 | 20.69 | 22.92 | 23.26 | 23.35 | 23.37 | 21.12 | 20.82 | 20.72
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-4C | 20.79 | 20.77 | 20.77 | 20.77 | 20.79 | 23.01 | 23.34 | 23.42 | 23.45 | 21.19 | 20.92 | 20.84
SmallHotel | 90.1-2013 | ASHRAE 169-2013-4C | 20.38 | 20.36 | 20.4 | 20.44 | 20.52 | 20.58 | 20.65 | 20.71 | 20.69 | 20.62 | 20.54 | 20.44
SmallOffice | 90.1-2013 | ASHRAE 169-2013-4C | 20.13 | 20.06 | 20.08 | 20.14 | 20.25 | 22.25 | 22.79 | 22.98 | 23.03 | 21.01 | 20.52 | 20.29
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-4C | 20.11 | 20.06 | 20.06 | 20.1 | 20.21 | 22.24 | 22.8 | 22.99 | 23.05 | 21.04 | 20.51 | 20.29
Warehouse | 90.1-2013 | ASHRAE 169-2013-4C | 12.65 | 12.64 | 12.66 | 12.69 | 12.91 | 15.02 | 17 | 18.18 | 15.36 | 13.12 | 12.83 | 12.72
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5A | 19.81 | 19.68 | 19.85 | 20.05 | 20.29 | 22.68 | 23.16 | 23.25 | 23.16 | 20.77 | 20.33 | 19.98
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-5A | 19.8 | 19.67 | 19.84 | 20.03 | 20.27 | 22.6 | 23.11 | 23.22 | 23.13 | 20.79 | 20.33 | 19.97
Hospital | 90.1-2004 | ASHRAE 169-2013-5A | 20.48 | 20.41 | 20.47 | 20.55 | 20.64 | 22.87 | 23.28 | 23.36 | 23.35 | 21.1 | 20.75 | 20.57
LargeHotel | 90.1-2004 | ASHRAE 169-2013-5A | 19.98 | 19.9 | 20.01 | 20.14 | 20.32 | 20.5 | 20.65 | 20.7 | 20.62 | 20.47 | 20.33 | 20.1
LargeOffice | 90.1-2004 | ASHRAE 169-2013-5A | 20.46 | 20.39 | 20.46 | 20.53 | 20.63 | 22.86 | 23.28 | 23.36 | 23.35 | 21.09 | 20.74 | 20.55
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-5A | 20.23 | 20.14 | 20.24 | 20.36 | 20.51 | 22.77 | 23.22 | 23.31 | 23.27 | 20.99 | 20.6 | 20.35
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-5A | 19.8 | 19.67 | 19.84 | 20.03 | 20.27 | 22.6 | 23.11 | 23.22 | 23.13 | 20.79 | 20.33 | 19.97
Outpatient | 90.1-2004 | ASHRAE 169-2013-5A | 19.96 | 19.86 | 20.01 | 20.17 | 20.37 | 21.41 | 21.7 | 21.76 | 21.68 | 20.65 | 20.37 | 20.1
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-5A | 20.38 | 20.31 | 20.39 | 20.48 | 20.6 | 22.9 | 23.3 | 23.38 | 23.35 | 21.03 | 20.69 | 20.48
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5A | 19.27 | 19.1 | 19.36 | 19.65 | 20.01 | 22.49 | 23.05 | 23.15 | 23 | 20.53 | 20.01 | 19.51
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-5A | 20.41 | 20.34 | 20.42 | 20.5 | 20.62 | 22.91 | 23.3 | 23.38 | 23.36 | 21.04 | 20.71 | 20.51
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-5A | 20.24 | 20.16 | 20.26 | 20.38 | 20.53 | 22.85 | 23.26 | 23.35 | 23.3 | 20.97 | 20.6 | 20.36
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-5A | 20.55 | 20.5 | 20.55 | 20.61 | 20.7 | 22.97 | 23.34 | 23.42 | 23.41 | 21.11 | 20.8 | 20.64
SmallHotel | 90.1-2004 | ASHRAE 169-2013-5A | 19.85 | 19.75 | 19.91 | 20.09 | 20.31 | 20.54 | 20.71 | 20.76 | 20.65 | 20.44 | 20.27 | 19.98
SmallOffice | 90.1-2004 | ASHRAE 169-2013-5A | 19.31 | 19.11 | 19.3 | 19.56 | 19.9 | 22.11 | 22.83 | 23.02 | 22.93 | 20.76 | 20.11 | 19.6
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
Warehouse | 90.1-2004 | ASHRAE 169-2013-5A | 12.6 | 12.53 | 12.57 | 12.63 | 13.43 | 17.47 | 20.78 | 20.24 | 16.81 | 13.33 | 12.9 | 12.7
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5A | 19.81 | 19.68 | 19.85 | 20.05 | 20.29 | 22.68 | 23.16 | 23.25 | 23.16 | 20.77 | 20.33 | 19.98
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-5A | 20.17 | 20.06 | 20.12 | 20.22 | 20.36 | 22.63 | 23.1 | 23.22 | 23.21 | 20.96 | 20.56 | 20.32
Hospital | 90.1-2007 | ASHRAE 169-2013-5A | 20.48 | 20.41 | 20.47 | 20.55 | 20.64 | 22.87 | 23.28 | 23.36 | 23.35 | 21.1 | 20.75 | 20.57
LargeHotel | 90.1-2007 | ASHRAE 169-2013-5A | 19.98 | 19.9 | 20.01 | 20.14 | 20.32 | 20.5 | 20.65 | 20.7 | 20.62 | 20.47 | 20.33 | 20.1
LargeOffice | 90.1-2007 | ASHRAE 169-2013-5A | 20.46 | 20.39 | 20.46 | 20.53 | 20.63 | 22.86 | 23.28 | 23.36 | 23.35 | 21.09 | 20.74 | 20.55
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-5A | 20.23 | 20.14 | 20.24 | 20.36 | 20.51 | 22.77 | 23.22 | 23.31 | 23.27 | 20.99 | 20.6 | 20.35
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-5A | 20.17 | 20.06 | 20.12 | 20.22 | 20.36 | 22.63 | 23.1 | 23.22 | 23.21 | 20.96 | 20.56 | 20.32
Outpatient | 90.1-2007 | ASHRAE 169-2013-5A | 19.96 | 19.86 | 20.01 | 20.17 | 20.37 | 21.41 | 21.7 | 21.76 | 21.68 | 20.65 | 20.37 | 20.1
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-5A | 20.38 | 20.31 | 20.39 | 20.48 | 20.6 | 22.9 | 23.3 | 23.38 | 23.35 | 21.03 | 20.69 | 20.48
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5A | 19.27 | 19.1 | 19.36 | 19.65 | 20.01 | 22.49 | 23.05 | 23.15 | 23 | 20.53 | 20.01 | 19.51
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-5A | 20.41 | 20.34 | 20.42 | 20.5 | 20.62 | 22.91 | 23.3 | 23.38 | 23.36 | 21.04 | 20.71 | 20.51
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-5A | 20.24 | 20.16 | 20.26 | 20.38 | 20.53 | 22.85 | 23.26 | 23.35 | 23.3 | 20.97 | 20.6 | 20.36
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-5A | 20.55 | 20.5 | 20.55 | 20.61 | 20.7 | 22.97 | 23.34 | 23.42 | 23.41 | 21.11 | 20.8 | 20.64
SmallHotel | 90.1-2007 | ASHRAE 169-2013-5A | 19.85 | 19.75 | 19.91 | 20.09 | 20.31 | 20.54 | 20.71 | 20.76 | 20.65 | 20.44 | 20.27 | 19.98
SmallOffice | 90.1-2007 | ASHRAE 169-2013-5A | 19.31 | 19.11 | 19.3 | 19.56 | 19.9 | 22.11 | 22.83 | 23.02 | 22.93 | 20.76 | 20.11 | 19.6
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
Warehouse | 90.1-2007 | ASHRAE 169-2013-5A | 12.6 | 12.53 | 12.57 | 12.63 | 13.43 | 17.47 | 20.78 | 20.24 | 16.81 | 13.33 | 12.9 | 12.7
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5A | 19.81 | 19.68 | 19.85 | 20.05 | 20.29 | 22.68 | 23.16 | 23.25 | 23.16 | 20.77 | 20.33 | 19.98
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-5A | 20.17 | 20.06 | 20.12 | 20.22 | 20.36 | 22.63 | 23.1 | 23.22 | 23.21 | 20.96 | 20.56 | 20.32
Hospital | 90.1-2010 | ASHRAE 169-2013-5A | 20.48 | 20.41 | 20.47 | 20.55 | 20.64 | 22.87 | 23.28 | 23.36 | 23.35 | 21.1 | 20.75 | 20.57
LargeHotel | 90.1-2010 | ASHRAE 169-2013-5A | 19.98 | 19.9 | 20.01 | 20.14 | 20.32 | 20.5 | 20.65 | 20.7 | 20.62 | 20.47 | 20.33 | 20.1
LargeOffice | 90.1-2010 | ASHRAE 169-2013-5A | 20.46 | 20.39 | 20.46 | 20.53 | 20.63 | 22.86 | 23.28 | 23.36 | 23.35 | 21.09 | 20.74 | 20.55
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-5A | 20.23 | 20.14 | 20.24 | 20.36 | 20.51 | 22.77 | 23.22 | 23.31 | 23.27 | 20.99 | 20.6 | 20.35
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-5A | 20.17 | 20.06 | 20.12 | 20.22 | 20.36 | 22.63 | 23.1 | 23.22 | 23.21 | 20.96 | 20.56 | 20.32
Outpatient | 90.1-2010 | ASHRAE 169-2013-5A | 19.96 | 19.86 | 20.01 | 20.17 | 20.37 | 21.41 | 21.7 | 21.76 | 21.68 | 20.65 | 20.37 | 20.1
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-5A | 20.38 | 20.31 | 20.39 | 20.48 | 20.6 | 22.9 | 23.3 | 23.38 | 23.35 | 21.03 | 20.69 | 20.48
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5A | 19.27 | 19.1 | 19.36 | 19.65 | 20.01 | 22.49 | 23.05 | 23.15 | 23 | 20.53 | 20.01 | 19.51
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-5A | 20.41 | 20.34 | 20.42 | 20.5 | 20.62 | 22.91 | 23.3 | 23.38 | 23.36 | 21.04 | 20.71 | 20.51
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-5A | 20.24 | 20.16 | 20.26 | 20.38 | 20.53 | 22.85 | 23.26 | 23.35 | 23.3 | 20.97 | 20.6 | 20.36
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-5A | 20.55 | 20.5 | 20.55 | 20.61 | 20.7 | 22.97 | 23.34 | 23.42 | 23.41 | 21.11 | 20.8 | 20.64
SmallHotel | 90.1-2010 | ASHRAE 169-2013-5A | 19.85 | 19.75 | 19.91 | 20.09 | 20.31 | 20.54 | 20.71 | 20.76 | 20.65 | 20.44 | 20.27 | 19.98
SmallOffice | 90.1-2010 | ASHRAE 169-2013-5A | 19.31 | 19.11 | 19.3 | 19.56 | 19.9 | 22.11 | 22.83 | 23.02 | 22.93 | 20.76 | 20.11 | 19.6
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
Warehouse | 90.1-2010 | ASHRAE 169-2013-5A | 12.6 | 12.53 | 12.57 | 12.63 | 13.43 | 17.47 | 20.78 | 20.24 | 16.81 | 13.33 | 12.9 | 12.7
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5A | 20.36 | 20.26 | 20.28 | 20.34 | 20.44 | 22.75 | 23.15 | 23.27 | 23.28 | 21 | 20.67 | 20.48
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-5A | 20.27 | 20.17 | 20.19 | 20.27 | 20.38 | 22.64 | 23.1 | 23.22 | 23.23 | 21 | 20.62 | 20.42
Hospital | 90.1-2013 | ASHRAE 169-2013-5A | 20.65 | 20.6 | 20.61 | 20.64 | 20.69 | 22.88 | 23.27 | 23.37 | 23.39 | 21.18 | 20.86 | 20.74
LargeHotel | 90.1-2013 | ASHRAE 169-2013-5A | 20.26 | 20.19 | 20.21 | 20.28 | 20.38 | 20.5 | 20.61 | 20.67 | 20.66 | 20.58 | 20.49 | 20.36
LargeOffice | 90.1-2013 | ASHRAE 169-2013-5A | 20.64 | 20.59 | 20.6 | 20.63 | 20.68 | 22.88 | 23.27 | 23.36 | 23.39 | 21.18 | 20.85 | 20.73
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-5A | 20.5 | 20.43 | 20.44 | 20.5 | 20.57 | 22.79 | 23.21 | 23.31 | 23.33 | 21.11 | 20.76 | 20.61
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5A | 20.49 | 20.43 | 20.44 | 20.5 | 20.59 | 22.83 | 23.24 | 23.33 | 23.36 | 21.14 | 20.78 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-5A | 20.27 | 20.17 | 20.19 | 20.27 | 20.38 | 22.64 | 23.1 | 23.22 | 23.23 | 21 | 20.62 | 20.42
Outpatient | 90.1-2013 | ASHRAE 169-2013-5A | 20.33 | 20.25 | 20.28 | 20.35 | 20.45 | 21.42 | 21.67 | 21.75 | 21.74 | 20.81 | 20.6 | 20.44
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-5A | 20.65 | 20.6 | 20.6 | 20.63 | 20.68 | 22.93 | 23.3 | 23.39 | 23.41 | 21.15 | 20.85 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5A | 20.09 | 19.97 | 20 | 20.09 | 20.23 | 22.59 | 23.04 | 23.18 | 23.18 | 20.88 | 20.51 | 20.27
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-5A | 20.67 | 20.62 | 20.62 | 20.65 | 20.69 | 22.94 | 23.3 | 23.39 | 23.42 | 21.15 | 20.86 | 20.75
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-5A | 20.58 | 20.52 | 20.52 | 20.56 | 20.62 | 22.89 | 23.26 | 23.36 | 23.38 | 21.11 | 20.81 | 20.67
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-5A | 20.75 | 20.7 | 20.7 | 20.72 | 20.75 | 22.99 | 23.34 | 23.42 | 23.45 | 21.19 | 20.91 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2013-5A | 20.24 | 20.16 | 20.21 | 20.29 | 20.41 | 20.54 | 20.66 | 20.73 | 20.7 | 20.61 | 20.51 | 20.36
SmallOffice | 90.1-2013 | ASHRAE 169-2013-5A | 19.94 | 19.77 | 19.79 | 19.9 | 20.07 | 22.18 | 22.81 | 23.02 | 23.06 | 21.02 | 20.49 | 20.17
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5A | 19.91 | 19.78 | 19.78 | 19.91 | 20.1 | 22.25 | 22.88 | 23.07 | 23.13 | 21.08 | 20.53 | 20.19
Warehouse | 90.1-2013 | ASHRAE 169-2013-5A | 12.6 | 12.53 | 12.57 | 12.63 | 13.43 | 17.47 | 20.78 | 20.24 | 16.81 | 13.33 | 12.9 | 12.7
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5B | 19.95 | 19.89 | 20.03 | 20.08 | 20.34 | 22.83 | 23.26 | 23.34 | 23.3 | 20.8 | 20.29 | 20
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-5B | 19.94 | 19.88 | 20.02 | 20.07 | 20.32 | 22.75 | 23.21 | 23.3 | 23.26 | 20.83 | 20.29 | 19.99
Hospital | 90.1-2004 | ASHRAE 169-2013-5B | 20.54 | 20.5 | 20.55 | 20.56 | 20.66 | 22.93 | 23.32 | 23.4 | 23.41 | 21.12 | 20.73 | 20.58
LargeHotel | 90.1-2004 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.14 | 20.18 | 20.36 | 20.61 | 20.73 | 20.76 | 20.72 | 20.5 | 20.3 | 20.12
LargeOffice | 90.1-2004 | ASHRAE 169-2013-5B | 20.52 | 20.48 | 20.54 | 20.55 | 20.66 | 22.92 | 23.32 | 23.4 | 23.4 | 21.11 | 20.72 | 20.57
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5B
MediumOffice | 90.1-2004 | ASHRAE 169-2013-5B | 20.32 | 20.27 | 20.35 | 20.38 | 20.54 | 22.86 | 23.28 | 23.36 | 23.35 | 21.01 | 20.57 | 20.37
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-5B | 19.94 | 19.88 | 20.02 | 20.07 | 20.32 | 22.75 | 23.21 | 23.3 | 23.26 | 20.83 | 20.29 | 19.99
Outpatient | 90.1-2004 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.15 | 20.2 | 20.41 | 21.53 | 21.78 | 21.83 | 21.78 | 20.68 | 20.34 | 20.12
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-5B | 20.46 | 20.41 | 20.48 | 20.5 | 20.63 | 22.98 | 23.35 | 23.42 | 23.42 | 21.05 | 20.67 | 20.5
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5B | 19.49 | 19.4 | 19.62 | 19.7 | 20.09 | 22.71 | 23.19 | 23.28 | 23.19 | 20.58 | 19.94 | 19.55
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-5B | 20.48 | 20.44 | 20.5 | 20.52 | 20.64 | 22.99 | 23.35 | 23.43 | 23.42 | 21.06 | 20.69 | 20.52
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-5B | 20.34 | 20.29 | 20.37 | 20.4 | 20.56 | 22.94 | 23.33 | 23.4 | 23.39 | 20.99 | 20.58 | 20.38
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-5B | 20.61 | 20.57 | 20.61 | 20.63 | 20.72 | 23.02 | 23.38 | 23.45 | 23.46 | 21.12 | 20.78 | 20.65
SmallHotel | 90.1-2004 | ASHRAE 169-2013-5B | 19.98 | 19.94 | 20.07 | 20.13 | 20.36 | 20.67 | 20.8 | 20.83 | 20.77 | 20.48 | 20.23 | 20.01
SmallOffice | 90.1-2004 | ASHRAE 169-2013-5B | 19.48 | 19.38 | 19.56 | 19.63 | 19.97 | 22.29 | 22.95 | 23.12 | 23.1 | 20.81 | 20.06 | 19.62
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
Warehouse | 90.1-2004 | ASHRAE 169-2013-5B | 12.68 | 12.62 | 12.65 | 12.65 | 13.46 | 20.37 | 21.76 | 21.22 | 18.64 | 13.56 | 12.94 | 12.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5B | 19.95 | 19.89 | 20.03 | 20.08 | 20.34 | 22.83 | 23.26 | 23.34 | 23.3 | 20.8 | 20.29 | 20
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-5B | 20.23 | 20.18 | 20.24 | 20.26 | 20.4 | 22.72 | 23.18 | 23.28 | 23.3 | 21 | 20.54 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2013-5B | 20.54 | 20.5 | 20.55 | 20.56 | 20.66 | 22.93 | 23.32 | 23.4 | 23.41 | 21.12 | 20.73 | 20.58
LargeHotel | 90.1-2007 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.14 | 20.18 | 20.36 | 20.61 | 20.73 | 20.76 | 20.72 | 20.5 | 20.3 | 20.12
LargeOffice | 90.1-2007 | ASHRAE 169-2013-5B | 20.52 | 20.48 | 20.54 | 20.55 | 20.66 | 22.92 | 23.32 | 23.4 | 23.4 | 21.11 | 20.72 | 20.57
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5B
MediumOffice | 90.1-2007 | ASHRAE 169-2013-5B | 20.32 | 20.27 | 20.35 | 20.38 | 20.54 | 22.86 | 23.28 | 23.36 | 23.35 | 21.01 | 20.57 | 20.37
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-5B | 20.23 | 20.18 | 20.24 | 20.26 | 20.4 | 22.72 | 23.18 | 23.28 | 23.3 | 21 | 20.54 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.15 | 20.2 | 20.41 | 21.53 | 21.78 | 21.83 | 21.78 | 20.68 | 20.34 | 20.12
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-5B | 20.46 | 20.41 | 20.48 | 20.5 | 20.63 | 22.98 | 23.35 | 23.42 | 23.42 | 21.05 | 20.67 | 20.5
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5B | 19.49 | 19.4 | 19.62 | 19.7 | 20.09 | 22.71 | 23.19 | 23.28 | 23.19 | 20.58 | 19.94 | 19.55
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-5B | 20.48 | 20.44 | 20.5 | 20.52 | 20.64 | 22.99 | 23.35 | 23.43 | 23.42 | 21.06 | 20.69 | 20.52
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-5B | 20.34 | 20.29 | 20.37 | 20.4 | 20.56 | 22.94 | 23.33 | 23.4 | 23.39 | 20.99 | 20.58 | 20.38
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-5B | 20.61 | 20.57 | 20.61 | 20.63 | 20.72 | 23.02 | 23.38 | 23.45 | 23.46 | 21.12 | 20.78 | 20.65
SmallHotel | 90.1-2007 | ASHRAE 169-2013-5B | 19.98 | 19.94 | 20.07 | 20.13 | 20.36 | 20.67 | 20.8 | 20.83 | 20.77 | 20.48 | 20.23 | 20.01
SmallOffice | 90.1-2007 | ASHRAE 169-2013-5B | 19.48 | 19.38 | 19.56 | 19.63 | 19.97 | 22.29 | 22.95 | 23.12 | 23.1 | 20.81 | 20.06 | 19.62
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
Warehouse | 90.1-2007 | ASHRAE 169-2013-5B | 12.68 | 12.62 | 12.65 | 12.65 | 13.46 | 20.37 | 21.76 | 21.22 | 18.64 | 13.56 | 12.94 | 12.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5B | 19.95 | 19.89 | 20.03 | 20.08 | 20.34 | 22.83 | 23.26 | 23.34 | 23.3 | 20.8 | 20.29 | 20
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-5B | 20.23 | 20.18 | 20.24 | 20.26 | 20.4 | 22.72 | 23.18 | 23.28 | 23.3 | 21 | 20.54 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2013-5B | 20.54 | 20.5 | 20.55 | 20.56 | 20.66 | 22.93 | 23.32 | 23.4 | 23.41 | 21.12 | 20.73 | 20.58
LargeHotel | 90.1-2010 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.14 | 20.18 | 20.36 | 20.61 | 20.73 | 20.76 | 20.72 | 20.5 | 20.3 | 20.12
LargeOffice | 90.1-2010 | ASHRAE 169-2013-5B | 20.52 | 20.48 | 20.54 | 20.55 | 20.66 | 22.92 | 23.32 | 23.4 | 23.4 | 21.11 | 20.72 | 20.57
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5B
MediumOffice | 90.1-2010 | ASHRAE 169-2013-5B | 20.32 | 20.27 | 20.35 | 20.38 | 20.54 | 22.86 | 23.28 | 23.36 | 23.35 | 21.01 | 20.57 | 20.37
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-5B | 20.23 | 20.18 | 20.24 | 20.26 | 20.4 | 22.72 | 23.18 | 23.28 | 23.3 | 21 | 20.54 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2013-5B | 20.08 | 20.04 | 20.15 | 20.2 | 20.41 | 21.53 | 21.78 | 21.83 | 21.78 | 20.68 | 20.34 | 20.12
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-5B | 20.46 | 20.41 | 20.48 | 20.5 | 20.63 | 22.98 | 23.35 | 23.42 | 23.42 | 21.05 | 20.67 | 20.5
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5B | 19.49 | 19.4 | 19.62 | 19.7 | 20.09 | 22.71 | 23.19 | 23.28 | 23.19 | 20.58 | 19.94 | 19.55
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-5B | 20.48 | 20.44 | 20.5 | 20.52 | 20.64 | 22.99 | 23.35 | 23.43 | 23.42 | 21.06 | 20.69 | 20.52
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-5B | 20.34 | 20.29 | 20.37 | 20.4 | 20.56 | 22.94 | 23.33 | 23.4 | 23.39 | 20.99 | 20.58 | 20.38
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-5B | 20.61 | 20.57 | 20.61 | 20.63 | 20.72 | 23.02 | 23.38 | 23.45 | 23.46 | 21.12 | 20.78 | 20.65
SmallHotel | 90.1-2010 | ASHRAE 169-2013-5B | 19.98 | 19.94 | 20.07 | 20.13 | 20.36 | 20.67 | 20.8 | 20.83 | 20.77 | 20.48 | 20.23 | 20.01
SmallOffice | 90.1-2010 | ASHRAE 169-2013-5B | 19.48 | 19.38 | 19.56 | 19.63 | 19.97 | 22.29 | 22.95 | 23.12 | 23.1 | 20.81 | 20.06 | 19.62
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
Warehouse | 90.1-2010 | ASHRAE 169-2013-5B | 12.68 | 12.62 | 12.65 | 12.65 | 13.46 | 20.37 | 21.76 | 21.22 | 18.64 | 13.56 | 12.94 | 12.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5B | 20.4 | 20.34 | 20.37 | 20.39 | 20.48 | 22.82 | 23.22 | 23.33 | 23.36 | 21.04 | 20.66 | 20.49
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-5B | 20.31 | 20.26 | 20.3 | 20.32 | 20.42 | 22.72 | 23.17 | 23.28 | 23.32 | 21.04 | 20.61 | 20.42
Hospital | 90.1-2013 | ASHRAE 169-2013-5B | 20.68 | 20.64 | 20.65 | 20.66 | 20.7 | 22.92 | 23.31 | 23.39 | 23.43 | 21.2 | 20.86 | 20.74
LargeHotel | 90.1-2013 | ASHRAE 169-2013-5B | 20.3 | 20.27 | 20.31 | 20.33 | 20.42 | 20.56 | 20.67 | 20.72 | 20.73 | 20.63 | 20.49 | 20.37
LargeOffice | 90.1-2013 | ASHRAE 169-2013-5B | 20.67 | 20.63 | 20.65 | 20.65 | 20.7 | 22.91 | 23.3 | 23.39 | 23.42 | 21.19 | 20.85 | 20.73
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5B
MediumOffice | 90.1-2013 | ASHRAE 169-2013-5B | 20.53 | 20.49 | 20.52 | 20.53 | 20.6 | 22.84 | 23.26 | 23.35 | 23.38 | 21.14 | 20.76 | 20.61
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5B | 20.5 | 20.5 | 20.51 | 20.55 | 20.62 | 22.83 | 23.26 | 23.37 | 23.37 | 21.14 | 20.76 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-5B | 20.31 | 20.26 | 20.3 | 20.32 | 20.42 | 22.72 | 23.17 | 23.28 | 23.32 | 21.04 | 20.61 | 20.42
Outpatient | 90.1-2013 | ASHRAE 169-2013-5B | 20.37 | 20.33 | 20.37 | 20.39 | 20.49 | 21.49 | 21.73 | 21.79 | 21.81 | 20.84 | 20.59 | 20.45
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-5B | 20.68 | 20.64 | 20.65 | 20.65 | 20.7 | 22.97 | 23.33 | 23.41 | 23.45 | 21.17 | 20.85 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5B | 20.15 | 20.08 | 20.13 | 20.15 | 20.29 | 22.68 | 23.13 | 23.25 | 23.29 | 20.94 | 20.5 | 20.28
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-5B | 20.69 | 20.66 | 20.66 | 20.67 | 20.71 | 22.98 | 23.34 | 23.42 | 23.45 | 21.17 | 20.86 | 20.75
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-5B | 20.61 | 20.57 | 20.58 | 20.59 | 20.65 | 22.93 | 23.3 | 23.39 | 23.43 | 21.14 | 20.81 | 20.68
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-5B | 20.76 | 20.73 | 20.73 | 20.73 | 20.77 | 23.02 | 23.36 | 23.44 | 23.48 | 21.21 | 20.91 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2013-5B | 20.29 | 20.26 | 20.31 | 20.33 | 20.45 | 20.61 | 20.73 | 20.78 | 20.78 | 20.65 | 20.5 | 20.36
SmallOffice | 90.1-2013 | ASHRAE 169-2013-5B | 19.99 | 19.89 | 19.94 | 19.98 | 20.13 | 22.28 | 22.9 | 23.1 | 23.16 | 21.07 | 20.48 | 20.17
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5B | 19.93 | 19.9 | 19.92 | 20.02 | 20.17 | 22.27 | 22.91 | 23.13 | 23.14 | 21.09 | 20.49 | 20.17
Warehouse | 90.1-2013 | ASHRAE 169-2013-5B | 12.68 | 12.62 | 12.65 | 12.65 | 13.46 | 20.37 | 21.76 | 21.22 | 18.64 | 13.56 | 12.94 | 12.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5C | 19.97 | 19.98 | 20 | 20.14 | 20.26 | 22.54 | 22.92 | 23.03 | 23 | 20.67 | 20.26 | 20.07
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-5C | 19.97 | 19.97 | 20 | 20.13 | 20.24 | 22.46 | 22.88 | 22.99 | 22.96 | 20.69 | 20.26 | 20.07
Hospital | 90.1-2004 | ASHRAE 169-2013-5C | 20.55 | 20.54 | 20.54 | 20.59 | 20.63 | 22.81 | 23.18 | 23.27 | 23.28 | 21.06 | 20.72 | 20.61
LargeHotel | 90.1-2004 | ASHRAE 169-2013-5C | 20.09 | 20.1 | 20.12 | 20.22 | 20.31 | 20.41 | 20.49 | 20.53 | 20.5 | 20.38 | 20.26 | 20.15
LargeOffice | 90.1-2004 | ASHRAE 169-2013-5C | 20.53 | 20.52 | 20.53 | 20.58 | 20.62 | 22.8 | 23.18 | 23.26 | 23.27 | 21.05 | 20.71 | 20.6
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5C
MediumOffice | 90.1-2004 | ASHRAE 169-2013-5C | 20.34 | 20.33 | 20.34 | 20.42 | 20.49 | 22.68 | 23.07 | 23.17 | 23.17 | 20.93 | 20.56 | 20.41
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-5C | 19.97 | 19.97 | 20 | 20.13 | 20.24 | 22.46 | 22.88 | 22.99 | 22.96 | 20.69 | 20.26 | 20.07
Outpatient | 90.1-2004 | ASHRAE 169-2013-5C | 20.1 | 20.11 | 20.14 | 20.25 | 20.35 | 21.29 | 21.51 | 21.57 | 21.54 | 20.57 | 20.32 | 20.18
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-5C | 20.46 | 20.46 | 20.46 | 20.53 | 20.59 | 22.83 | 23.18 | 23.26 | 23.26 | 20.98 | 20.65 | 20.53
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-5C | 19.52 | 19.54 | 19.58 | 19.79 | 19.97 | 22.28 | 22.69 | 22.82 | 22.76 | 20.38 | 19.91 | 19.65
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-5C | 20.49 | 20.48 | 20.49 | 20.55 | 20.6 | 22.84 | 23.19 | 23.27 | 23.28 | 20.99 | 20.67 | 20.55
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-5C | 20.34 | 20.34 | 20.35 | 20.44 | 20.51 | 22.76 | 23.11 | 23.2 | 23.2 | 20.9 | 20.56 | 20.42
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-5C | 20.61 | 20.6 | 20.6 | 20.65 | 20.69 | 22.92 | 23.26 | 23.33 | 23.35 | 21.07 | 20.77 | 20.67
SmallHotel | 90.1-2004 | ASHRAE 169-2013-5C | 20 | 20.02 | 20.06 | 20.19 | 20.29 | 20.41 | 20.5 | 20.55 | 20.5 | 20.35 | 20.21 | 20.07
SmallOffice | 90.1-2004 | ASHRAE 169-2013-5C | 19.55 | 19.54 | 19.57 | 19.74 | 19.9 | 21.95 | 22.52 | 22.7 | 22.69 | 20.6 | 20.02 | 19.72
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
Warehouse | 90.1-2004 | ASHRAE 169-2013-5C | 12.56 | 12.56 | 12.56 | 12.62 | 12.66 | 13.12 | 14.55 | 15.32 | 13.56 | 12.82 | 12.68 | 12.61
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5C | 19.97 | 19.98 | 20 | 20.14 | 20.26 | 22.54 | 22.92 | 23.03 | 23 | 20.67 | 20.26 | 20.07
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-5C | 20.23 | 20.21 | 20.21 | 20.28 | 20.36 | 22.56 | 22.96 | 23.07 | 23.09 | 20.86 | 20.48 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2013-5C | 20.55 | 20.54 | 20.54 | 20.59 | 20.63 | 22.81 | 23.18 | 23.27 | 23.28 | 21.06 | 20.72 | 20.61
LargeHotel | 90.1-2007 | ASHRAE 169-2013-5C | 20.09 | 20.1 | 20.12 | 20.22 | 20.31 | 20.41 | 20.49 | 20.53 | 20.5 | 20.38 | 20.26 | 20.15
LargeOffice | 90.1-2007 | ASHRAE 169-2013-5C | 20.53 | 20.52 | 20.53 | 20.58 | 20.62 | 22.8 | 23.18 | 23.26 | 23.27 | 21.05 | 20.71 | 20.6
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5C
MediumOffice | 90.1-2007 | ASHRAE 169-2013-5C | 20.34 | 20.33 | 20.34 | 20.42 | 20.49 | 22.68 | 23.07 | 23.17 | 23.17 | 20.93 | 20.56 | 20.41
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-5C | 20.23 | 20.21 | 20.21 | 20.28 | 20.36 | 22.56 | 22.96 | 23.07 | 23.09 | 20.86 | 20.48 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2013-5C | 20.1 | 20.11 | 20.14 | 20.25 | 20.35 | 21.29 | 21.51 | 21.57 | 21.54 | 20.57 | 20.32 | 20.18
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-5C | 20.46 | 20.46 | 20.46 | 20.53 | 20.59 | 22.83 | 23.18 | 23.26 | 23.26 | 20.98 | 20.65 | 20.53
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-5C | 19.52 | 19.54 | 19.58 | 19.79 | 19.97 | 22.28 | 22.69 | 22.82 | 22.76 | 20.38 | 19.91 | 19.65
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-5C | 20.49 | 20.48 | 20.49 | 20.55 | 20.6 | 22.84 | 23.19 | 23.27 | 23.28 | 20.99 | 20.67 | 20.55
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-5C | 20.34 | 20.34 | 20.35 | 20.44 | 20.51 | 22.76 | 23.11 | 23.2 | 23.2 | 20.9 | 20.56 | 20.42
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-5C | 20.61 | 20.6 | 20.6 | 20.65 | 20.69 | 22.92 | 23.26 | 23.33 | 23.35 | 21.07 | 20.77 | 20.67
SmallHotel | 90.1-2007 | ASHRAE 169-2013-5C | 20 | 20.02 | 20.06 | 20.19 | 20.29 | 20.41 | 20.5 | 20.55 | 20.5 | 20.35 | 20.21 | 20.07
SmallOffice | 90.1-2007 | ASHRAE 169-2013-5C | 19.55 | 19.54 | 19.57 | 19.74 | 19.9 | 21.95 | 22.52 | 22.7 | 22.69 | 20.6 | 20.02 | 19.72
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
Warehouse | 90.1-2007 | ASHRAE 169-2013-5C | 12.56 | 12.56 | 12.56 | 12.62 | 12.66 | 13.12 | 14.55 | 15.32 | 13.56 | 12.82 | 12.68 | 12.61
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5C | 19.97 | 19.98 | 20 | 20.14 | 20.26 | 22.54 | 22.92 | 23.03 | 23 | 20.67 | 20.26 | 20.07
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-5C | 20.23 | 20.21 | 20.21 | 20.28 | 20.36 | 22.56 | 22.96 | 23.07 | 23.09 | 20.86 | 20.48 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2013-5C | 20.55 | 20.54 | 20.54 | 20.59 | 20.63 | 22.81 | 23.18 | 23.27 | 23.28 | 21.06 | 20.72 | 20.61
LargeHotel | 90.1-2010 | ASHRAE 169-2013-5C | 20.09 | 20.1 | 20.12 | 20.22 | 20.31 | 20.41 | 20.49 | 20.53 | 20.5 | 20.38 | 20.26 | 20.15
LargeOffice | 90.1-2010 | ASHRAE 169-2013-5C | 20.53 | 20.52 | 20.53 | 20.58 | 20.62 | 22.8 | 23.18 | 23.26 | 23.27 | 21.05 | 20.71 | 20.6
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5C
MediumOffice | 90.1-2010 | ASHRAE 169-2013-5C | 20.34 | 20.33 | 20.34 | 20.42 | 20.49 | 22.68 | 23.07 | 23.17 | 23.17 | 20.93 | 20.56 | 20.41
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-5C | 20.23 | 20.21 | 20.21 | 20.28 | 20.36 | 22.56 | 22.96 | 23.07 | 23.09 | 20.86 | 20.48 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2013-5C | 20.1 | 20.11 | 20.14 | 20.25 | 20.35 | 21.29 | 21.51 | 21.57 | 21.54 | 20.57 | 20.32 | 20.18
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-5C | 20.46 | 20.46 | 20.46 | 20.53 | 20.59 | 22.83 | 23.18 | 23.26 | 23.26 | 20.98 | 20.65 | 20.53
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-5C | 19.52 | 19.54 | 19.58 | 19.79 | 19.97 | 22.28 | 22.69 | 22.82 | 22.76 | 20.38 | 19.91 | 19.65
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-5C | 20.49 | 20.48 | 20.49 | 20.55 | 20.6 | 22.84 | 23.19 | 23.27 | 23.28 | 20.99 | 20.67 | 20.55
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-5C | 20.34 | 20.34 | 20.35 | 20.44 | 20.51 | 22.76 | 23.11 | 23.2 | 23.2 | 20.9 | 20.56 | 20.42
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-5C | 20.61 | 20.6 | 20.6 | 20.65 | 20.69 | 22.92 | 23.26 | 23.33 | 23.35 | 21.07 | 20.77 | 20.67
SmallHotel | 90.1-2010 | ASHRAE 169-2013-5C | 20 | 20.02 | 20.06 | 20.19 | 20.29 | 20.41 | 20.5 | 20.55 | 20.5 | 20.35 | 20.21 | 20.07
SmallOffice | 90.1-2010 | ASHRAE 169-2013-5C | 19.55 | 19.54 | 19.57 | 19.74 | 19.9 | 21.95 | 22.52 | 22.7 | 22.69 | 20.6 | 20.02 | 19.72
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
Warehouse | 90.1-2010 | ASHRAE 169-2013-5C | 12.56 | 12.56 | 12.56 | 12.62 | 12.66 | 13.12 | 14.55 | 15.32 | 13.56 | 12.82 | 12.68 | 12.61
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5C | 20.38 | 20.35 | 20.34 | 20.39 | 20.45 | 22.7 | 23.06 | 23.15 | 23.18 | 20.92 | 20.59 | 20.47
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-5C | 20.3 | 20.28 | 20.27 | 20.32 | 20.39 | 22.59 | 22.98 | 23.09 | 23.12 | 20.91 | 20.54 | 20.4
Hospital | 90.1-2013 | ASHRAE 169-2013-5C | 20.67 | 20.65 | 20.64 | 20.66 | 20.69 | 22.86 | 23.22 | 23.31 | 23.34 | 21.14 | 20.83 | 20.73
LargeHotel | 90.1-2013 | ASHRAE 169-2013-5C | 20.29 | 20.28 | 20.28 | 20.33 | 20.39 | 20.46 | 20.52 | 20.56 | 20.56 | 20.51 | 20.43 | 20.35
LargeOffice | 90.1-2013 | ASHRAE 169-2013-5C | 20.66 | 20.64 | 20.63 | 20.65 | 20.68 | 22.85 | 23.22 | 23.3 | 23.34 | 21.14 | 20.82 | 20.73
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5C
MediumOffice | 90.1-2013 | ASHRAE 169-2013-5C | 20.53 | 20.51 | 20.5 | 20.53 | 20.58 | 22.76 | 23.13 | 23.23 | 23.26 | 21.05 | 20.72 | 20.6
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5C | 20.54 | 20.52 | 20.52 | 20.55 | 20.6 | 22.79 | 23.17 | 23.26 | 23.29 | 21.07 | 20.73 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-5C | 20.3 | 20.28 | 20.27 | 20.32 | 20.39 | 22.59 | 22.98 | 23.09 | 23.12 | 20.91 | 20.54 | 20.4
Outpatient | 90.1-2013 | ASHRAE 169-2013-5C | 20.36 | 20.35 | 20.35 | 20.4 | 20.46 | 21.38 | 21.57 | 21.63 | 21.64 | 20.73 | 20.53 | 20.43
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-5C | 20.67 | 20.64 | 20.63 | 20.65 | 20.68 | 22.91 | 23.24 | 23.33 | 23.36 | 21.1 | 20.82 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-5C | 20.12 | 20.1 | 20.08 | 20.15 | 20.25 | 22.52 | 22.89 | 23.01 | 23.04 | 20.77 | 20.4 | 20.24
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-5C | 20.68 | 20.66 | 20.65 | 20.67 | 20.69 | 22.92 | 23.25 | 23.34 | 23.37 | 21.11 | 20.83 | 20.74
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-5C | 20.59 | 20.57 | 20.56 | 20.59 | 20.62 | 22.86 | 23.2 | 23.28 | 23.31 | 21.06 | 20.76 | 20.66
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-5C | 20.76 | 20.74 | 20.72 | 20.73 | 20.75 | 22.98 | 23.3 | 23.38 | 23.41 | 21.16 | 20.89 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2013-5C | 20.28 | 20.28 | 20.28 | 20.34 | 20.41 | 20.49 | 20.55 | 20.6 | 20.59 | 20.53 | 20.44 | 20.35
SmallOffice | 90.1-2013 | ASHRAE 169-2013-5C | 19.99 | 19.94 | 19.93 | 20 | 20.11 | 22.13 | 22.66 | 22.83 | 22.89 | 20.88 | 20.38 | 20.15
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-5C | 20.01 | 19.97 | 19.96 | 20.04 | 20.16 | 22.19 | 22.75 | 22.92 | 22.96 | 20.93 | 20.41 | 20.16
Warehouse | 90.1-2013 | ASHRAE 169-2013-5C | 12.56 | 12.56 | 12.56 | 12.62 | 12.66 | 13.12 | 14.55 | 15.32 | 13.56 | 12.82 | 12.68 | 12.61
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-6A | 19.47 | 19.42 | 19.66 | 19.95 | 20.23 | 22.64 | 23.12 | 23.2 | 23.13 | 20.66 | 20.14 | 19.7
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-6A | 19.46 | 19.4 | 19.64 | 19.93 | 20.21 | 22.56 | 23.07 | 23.15 | 23.1 | 20.68 | 20.13 | 19.69
Hospital | 90.1-2004 | ASHRAE 169-2013-6A | 20.34 | 20.3 | 20.39 | 20.5 | 20.62 | 22.85 | 23.26 | 23.34 | 23.34 | 21.05 | 20.67 | 20.45
LargeHotel | 90.1-2004 | ASHRAE 169-2013-6A | 19.74 | 19.69 | 19.85 | 20.06 | 20.27 | 20.46 | 20.61 | 20.65 | 20.6 | 20.38 | 20.19 | 19.9
LargeOffice | 90.1-2004 | ASHRAE 169-2013-6A | 20.32 | 20.28 | 20.37 | 20.49 | 20.61 | 22.84 | 23.26 | 23.33 | 23.33 | 21.04 | 20.66 | 20.43
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-6A | 20.02 | 19.98 | 20.12 | 20.29 | 20.47 | 22.74 | 23.19 | 23.27 | 23.25 | 20.92 | 20.47 | 20.18
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6A | 20.12 | 20.06 | 20.1 | 20.27 | 20.5 | 22.72 | 23.17 | 23.26 | 23.22 | 20.97 | 20.52 | 20.28
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-6A | 19.46 | 19.4 | 19.64 | 19.93 | 20.21 | 22.56 | 23.07 | 23.15 | 23.1 | 20.68 | 20.13 | 19.69
Outpatient | 90.1-2004 | ASHRAE 169-2013-6A | 19.69 | 19.64 | 19.84 | 20.08 | 20.32 | 21.37 | 21.66 | 21.71 | 21.65 | 20.55 | 20.21 | 19.87
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-6A | 20.21 | 20.17 | 20.29 | 20.43 | 20.57 | 22.88 | 23.27 | 23.35 | 23.33 | 20.97 | 20.59 | 20.34
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-6A | 18.79 | 18.72 | 19.08 | 19.51 | 19.93 | 22.44 | 22.99 | 23.07 | 22.96 | 20.37 | 19.73 | 19.11
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-6A | 20.25 | 20.21 | 20.32 | 20.46 | 20.59 | 22.89 | 23.28 | 23.35 | 23.34 | 20.99 | 20.61 | 20.38
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-6A | 20.04 | 19.99 | 20.14 | 20.31 | 20.49 | 22.82 | 23.23 | 23.31 | 23.28 | 20.9 | 20.48 | 20.19
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-6A | 20.43 | 20.4 | 20.48 | 20.58 | 20.67 | 22.95 | 23.32 | 23.39 | 23.4 | 21.07 | 20.73 | 20.54
SmallHotel | 90.1-2004 | ASHRAE 169-2013-6A | 19.55 | 19.51 | 19.73 | 20 | 20.26 | 20.5 | 20.67 | 20.7 | 20.62 | 20.34 | 20.09 | 19.73
SmallOffice | 90.1-2004 | ASHRAE 169-2013-6A | 18.86 | 18.71 | 19 | 19.4 | 19.81 | 22.06 | 22.78 | 22.94 | 22.9 | 20.6 | 19.87 | 19.22
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6A | 19.1 | 18.94 | 18.99 | 19.35 | 19.86 | 22.01 | 22.73 | 22.93 | 22.83 | 20.71 | 19.98 | 19.46
Warehouse | 90.1-2004 | ASHRAE 169-2013-6A | 12.47 | 12.42 | 12.5 | 12.59 | 13.8 | 17.98 | 19.96 | 19.57 | 15.82 | 13.18 | 12.8 | 12.59
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-6A | 20.09 | 20 | 20.08 | 20.21 | 20.36 | 22.69 | 23.12 | 23.22 | 23.24 | 20.91 | 20.52 | 20.26
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-6A | 20.04 | 19.93 | 20.02 | 20.16 | 20.31 | 22.59 | 23.06 | 23.18 | 23.2 | 20.91 | 20.5 | 20.21
Hospital | 90.1-2007 | ASHRAE 169-2013-6A | 20.54 | 20.48 | 20.52 | 20.58 | 20.65 | 22.86 | 23.26 | 23.35 | 23.37 | 21.14 | 20.8 | 20.63
LargeHotel | 90.1-2007 | ASHRAE 169-2013-6A | 20.05 | 19.97 | 20.06 | 20.18 | 20.32 | 20.46 | 20.58 | 20.63 | 20.63 | 20.5 | 20.38 | 20.18
LargeOffice | 90.1-2007 | ASHRAE 169-2013-6A | 20.52 | 20.47 | 20.51 | 20.57 | 20.64 | 22.85 | 23.25 | 23.34 | 23.37 | 21.13 | 20.79 | 20.62
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-6A | 20.33 | 20.25 | 20.32 | 20.41 | 20.52 | 22.76 | 23.18 | 23.28 | 23.3 | 21.04 | 20.67 | 20.45
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-6A | 20.04 | 19.93 | 20.02 | 20.16 | 20.31 | 22.59 | 23.06 | 23.18 | 23.2 | 20.91 | 20.5 | 20.21
Outpatient | 90.1-2007 | ASHRAE 169-2013-6A | 20.1 | 20.02 | 20.11 | 20.25 | 20.39 | 21.38 | 21.64 | 21.71 | 21.71 | 20.72 | 20.47 | 20.24
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-6A | 20.51 | 20.46 | 20.5 | 20.56 | 20.63 | 22.9 | 23.27 | 23.36 | 23.39 | 21.09 | 20.78 | 20.61
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-6A | 19.72 | 19.59 | 19.71 | 19.9 | 20.12 | 22.5 | 22.98 | 23.11 | 23.12 | 20.74 | 20.3 | 19.94
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-6A | 20.54 | 20.49 | 20.52 | 20.58 | 20.65 | 22.92 | 23.28 | 23.37 | 23.39 | 21.1 | 20.79 | 20.64
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-6A | 20.41 | 20.35 | 20.39 | 20.47 | 20.56 | 22.85 | 23.23 | 23.33 | 23.35 | 21.05 | 20.71 | 20.53
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-6A | 20.65 | 20.6 | 20.63 | 20.67 | 20.72 | 22.97 | 23.33 | 23.4 | 23.43 | 21.15 | 20.86 | 20.73
SmallHotel | 90.1-2007 | ASHRAE 169-2013-6A | 20 | 19.92 | 20.02 | 20.17 | 20.33 | 20.49 | 20.64 | 20.68 | 20.67 | 20.52 | 20.37 | 20.14
SmallOffice | 90.1-2007 | ASHRAE 169-2013-6A | 19.56 | 19.38 | 19.49 | 19.7 | 19.95 | 22.1 | 22.76 | 22.96 | 23 | 20.88 | 20.29 | 19.84
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
Warehouse | 90.1-2007 | ASHRAE 169-2013-6A | 12.47 | 12.42 | 12.5 | 12.59 | 13.8 | 17.98 | 19.96 | 19.57 | 15.82 | 13.18 | 12.8 | 12.59
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-6A | 20.09 | 20 | 20.08 | 20.21 | 20.36 | 22.69 | 23.12 | 23.22 | 23.24 | 20.91 | 20.52 | 20.26
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-6A | 20.04 | 19.93 | 20.02 | 20.16 | 20.31 | 22.59 | 23.06 | 23.18 | 23.2 | 20.91 | 20.5 | 20.21
Hospital | 90.1-2010 | ASHRAE 169-2013-6A | 20.54 | 20.48 | 20.52 | 20.58 | 20.65 | 22.86 | 23.26 | 23.35 | 23.37 | 21.14 | 20.8 | 20.63
LargeHotel | 90.1-2010 | ASHRAE 169-2013-6A | 20.05 | 19.97 | 20.06 | 20.18 | 20.32 | 20.46 | 20.58 | 20.63 | 20.63 | 20.5 | 20.38 | 20.18
LargeOffice | 90.1-2010 | ASHRAE 169-2013-6A | 20.52 | 20.47 | 20.51 | 20.57 | 20.64 | 22.85 | 23.25 | 23.34 | 23.37 | 21.13 | 20.79 | 20.62
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-6A | 20.33 | 20.25 | 20.32 | 20.41 | 20.52 | 22.76 | 23.18 | 23.28 | 23.3 | 21.04 | 20.67 | 20.45
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-6A | 20.04 | 19.93 | 20.02 | 20.16 | 20.31 | 22.59 | 23.06 | 23.18 | 23.2 | 20.91 | 20.5 | 20.21
Outpatient | 90.1-2010 | ASHRAE 169-2013-6A | 20.1 | 20.02 | 20.11 | 20.25 | 20.39 | 21.38 | 21.64 | 21.71 | 21.71 | 20.72 | 20.47 | 20.24
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-6A | 20.51 | 20.46 | 20.5 | 20.56 | 20.63 | 22.9 | 23.27 | 23.36 | 23.39 | 21.09 | 20.78 | 20.61
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-6A | 19.72 | 19.59 | 19.71 | 19.9 | 20.12 | 22.5 | 22.98 | 23.11 | 23.12 | 20.74 | 20.3 | 19.94
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-6A | 20.54 | 20.49 | 20.52 | 20.58 | 20.65 | 22.92 | 23.28 | 23.37 | 23.39 | 21.1 | 20.79 | 20.64
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-6A | 20.41 | 20.35 | 20.39 | 20.47 | 20.56 | 22.85 | 23.23 | 23.33 | 23.35 | 21.05 | 20.71 | 20.53
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-6A | 20.65 | 20.6 | 20.63 | 20.67 | 20.72 | 22.97 | 23.33 | 23.4 | 23.43 | 21.15 | 20.86 | 20.73
SmallHotel | 90.1-2010 | ASHRAE 169-2013-6A | 20 | 19.92 | 20.02 | 20.17 | 20.33 | 20.49 | 20.64 | 20.68 | 20.67 | 20.52 | 20.37 | 20.14
SmallOffice | 90.1-2010 | ASHRAE 169-2013-6A | 19.56 | 19.38 | 19.49 | 19.7 | 19.95 | 22.1 | 22.76 | 22.96 | 23 | 20.88 | 20.29 | 19.84
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
Warehouse | 90.1-2010 | ASHRAE 169-2013-6A | 12.47 | 12.42 | 12.5 | 12.59 | 13.8 | 17.98 | 19.96 | 19.57 | 15.82 | 13.18 | 12.8 | 12.59
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-6A | 20.26 | 20.16 | 20.19 | 20.28 | 20.39 | 22.7 | 23.12 | 23.23 | 23.27 | 20.97 | 20.62 | 20.41
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-6A | 20.23 | 20.13 | 20.17 | 20.26 | 20.37 | 22.62 | 23.07 | 23.19 | 23.23 | 20.99 | 20.6 | 20.38
Hospital | 90.1-2013 | ASHRAE 169-2013-6A | 20.6 | 20.54 | 20.56 | 20.61 | 20.66 | 22.86 | 23.26 | 23.35 | 23.38 | 21.16 | 20.83 | 20.68
LargeHotel | 90.1-2013 | ASHRAE 169-2013-6A | 20.14 | 20.06 | 20.11 | 20.22 | 20.33 | 20.46 | 20.58 | 20.63 | 20.64 | 20.54 | 20.44 | 20.26
LargeOffice | 90.1-2013 | ASHRAE 169-2013-6A | 20.58 | 20.52 | 20.55 | 20.6 | 20.65 | 22.86 | 23.25 | 23.34 | 23.38 | 21.15 | 20.82 | 20.67
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-6A | 20.41 | 20.33 | 20.37 | 20.45 | 20.54 | 22.76 | 23.18 | 23.28 | 23.32 | 21.08 | 20.72 | 20.53
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6A | 20.45 | 20.38 | 20.36 | 20.43 | 20.54 | 22.76 | 23.17 | 23.28 | 23.3 | 21.09 | 20.74 | 20.57
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-6A | 20.23 | 20.13 | 20.17 | 20.26 | 20.37 | 22.62 | 23.07 | 23.19 | 23.23 | 20.99 | 20.6 | 20.38
Outpatient | 90.1-2013 | ASHRAE 169-2013-6A | 20.22 | 20.13 | 20.19 | 20.29 | 20.41 | 21.38 | 21.63 | 21.71 | 21.72 | 20.76 | 20.54 | 20.34
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-6A | 20.6 | 20.54 | 20.56 | 20.6 | 20.65 | 22.91 | 23.28 | 23.36 | 23.4 | 21.13 | 20.83 | 20.69
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-6A | 19.95 | 19.82 | 19.87 | 20 | 20.17 | 22.53 | 22.99 | 23.12 | 23.16 | 20.84 | 20.44 | 20.15
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-6A | 20.62 | 20.57 | 20.58 | 20.61 | 20.67 | 22.92 | 23.28 | 23.37 | 23.41 | 21.14 | 20.84 | 20.71
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-6A | 20.52 | 20.45 | 20.47 | 20.52 | 20.59 | 22.86 | 23.24 | 23.33 | 23.37 | 21.09 | 20.78 | 20.62
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-6A | 20.71 | 20.66 | 20.67 | 20.7 | 20.73 | 22.98 | 23.33 | 23.41 | 23.44 | 21.18 | 20.89 | 20.78
SmallHotel | 90.1-2013 | ASHRAE 169-2013-6A | 20.12 | 20.03 | 20.1 | 20.22 | 20.36 | 20.5 | 20.63 | 20.68 | 20.68 | 20.56 | 20.45 | 20.24
SmallOffice | 90.1-2013 | ASHRAE 169-2013-6A | 19.75 | 19.57 | 19.63 | 19.78 | 19.99 | 22.12 | 22.76 | 22.97 | 23.04 | 20.96 | 20.41 | 20.02
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6A | 19.84 | 19.68 | 19.63 | 19.75 | 20 | 22.1 | 22.73 | 22.96 | 23 | 20.99 | 20.44 | 20.12
Warehouse | 90.1-2013 | ASHRAE 169-2013-6A | 12.47 | 12.42 | 12.5 | 12.59 | 13.8 | 17.98 | 19.96 | 19.57 | 15.82 | 13.18 | 12.8 | 12.59
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-6B | 19.57 | 19.63 | 19.78 | 20 | 20.12 | 22.57 | 23.09 | 23.18 | 23.08 | 20.69 | 20.22 | 19.9
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-6B | 19.56 | 19.61 | 19.76 | 19.98 | 20.1 | 22.49 | 23.04 | 23.14 | 23.04 | 20.71 | 20.22 | 19.89
Hospital | 90.1-2004 | ASHRAE 169-2013-6B | 20.38 | 20.39 | 20.44 | 20.53 | 20.57 | 22.82 | 23.25 | 23.33 | 23.31 | 21.07 | 20.7 | 20.54
LargeHotel | 90.1-2004 | ASHRAE 169-2013-6B | 19.81 | 19.83 | 19.95 | 20.1 | 20.19 | 20.41 | 20.59 | 20.64 | 20.56 | 20.4 | 20.24 | 20.04
LargeOffice | 90.1-2004 | ASHRAE 169-2013-6B | 20.36 | 20.37 | 20.42 | 20.51 | 20.56 | 22.81 | 23.24 | 23.33 | 23.31 | 21.06 | 20.69 | 20.52
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6B
MediumOffice | 90.1-2004 | ASHRAE 169-2013-6B | 20.08 | 20.11 | 20.19 | 20.33 | 20.4 | 22.7 | 23.17 | 23.26 | 23.21 | 20.93 | 20.53 | 20.3
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6B | 20.1 | 20.12 | 20.16 | 20.29 | 20.43 | 22.68 | 23.18 | 23.25 | 23.21 | 20.93 | 20.49 | 20.23
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-6B | 19.56 | 19.61 | 19.76 | 19.98 | 20.1 | 22.49 | 23.04 | 23.14 | 23.04 | 20.71 | 20.22 | 19.89
Outpatient | 90.1-2004 | ASHRAE 169-2013-6B | 19.77 | 19.82 | 19.94 | 20.13 | 20.23 | 21.31 | 21.63 | 21.7 | 21.6 | 20.58 | 20.28 | 20.03
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-6B | 20.26 | 20.28 | 20.35 | 20.46 | 20.52 | 22.84 | 23.26 | 23.34 | 23.3 | 20.99 | 20.63 | 20.44
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-6B | 18.94 | 19.03 | 19.25 | 19.59 | 19.77 | 22.33 | 22.94 | 23.05 | 22.88 | 20.41 | 19.85 | 19.4
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-6B | 20.3 | 20.31 | 20.38 | 20.48 | 20.54 | 22.86 | 23.27 | 23.35 | 23.32 | 21 | 20.65 | 20.47
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-6B | 20.1 | 20.12 | 20.21 | 20.35 | 20.42 | 22.78 | 23.22 | 23.3 | 23.25 | 20.91 | 20.53 | 20.31
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-6B | 20.47 | 20.48 | 20.52 | 20.6 | 20.64 | 22.93 | 23.31 | 23.39 | 23.38 | 21.08 | 20.75 | 20.61
SmallHotel | 90.1-2004 | ASHRAE 169-2013-6B | 19.64 | 19.7 | 19.84 | 20.05 | 20.16 | 20.44 | 20.65 | 20.69 | 20.57 | 20.36 | 20.16 | 19.91
SmallOffice | 90.1-2004 | ASHRAE 169-2013-6B | 19.01 | 19 | 19.19 | 19.49 | 19.68 | 21.95 | 22.71 | 22.91 | 22.81 | 20.63 | 19.96 | 19.49
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-6B | 19.02 | 19.05 | 19.11 | 19.42 | 19.74 | 21.91 | 22.73 | 22.9 | 22.82 | 20.61 | 19.89 | 19.33
Warehouse | 90.1-2004 | ASHRAE 169-2013-6B | 12.48 | 12.49 | 12.53 | 12.6 | 12.63 | 15.67 | 19.39 | 18.82 | 15.11 | 13.08 | 12.79 | 12.63
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-6B | 20.15 | 20.11 | 20.16 | 20.26 | 20.32 | 22.66 | 23.1 | 23.21 | 23.21 | 20.91 | 20.55 | 20.35
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-6B | 20.09 | 20.04 | 20.1 | 20.2 | 20.27 | 22.56 | 23.03 | 23.17 | 23.17 | 20.92 | 20.53 | 20.32
Hospital | 90.1-2007 | ASHRAE 169-2013-6B | 20.56 | 20.54 | 20.56 | 20.6 | 20.63 | 22.84 | 23.25 | 23.34 | 23.36 | 21.14 | 20.81 | 20.68
LargeHotel | 90.1-2007 | ASHRAE 169-2013-6B | 20.1 | 20.07 | 20.13 | 20.22 | 20.29 | 20.43 | 20.56 | 20.63 | 20.6 | 20.51 | 20.41 | 20.27
LargeOffice | 90.1-2007 | ASHRAE 169-2013-6B | 20.55 | 20.52 | 20.55 | 20.59 | 20.62 | 22.84 | 23.24 | 23.34 | 23.35 | 21.13 | 20.8 | 20.67
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6B
MediumOffice | 90.1-2007 | ASHRAE 169-2013-6B | 20.37 | 20.33 | 20.37 | 20.45 | 20.49 | 22.73 | 23.17 | 23.27 | 23.28 | 21.05 | 20.69 | 20.53
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-6B | 20.09 | 20.04 | 20.1 | 20.2 | 20.27 | 22.56 | 23.03 | 23.17 | 23.17 | 20.92 | 20.53 | 20.32
Outpatient | 90.1-2007 | ASHRAE 169-2013-6B | 20.15 | 20.13 | 20.19 | 20.29 | 20.35 | 21.35 | 21.61 | 21.7 | 21.68 | 20.72 | 20.5 | 20.34
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-6B | 20.54 | 20.52 | 20.54 | 20.58 | 20.61 | 22.89 | 23.26 | 23.36 | 23.37 | 21.1 | 20.79 | 20.67
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-6B | 19.79 | 19.75 | 19.83 | 19.97 | 20.07 | 22.46 | 22.95 | 23.1 | 23.08 | 20.75 | 20.35 | 20.08
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-6B | 20.57 | 20.54 | 20.56 | 20.6 | 20.63 | 22.9 | 23.27 | 23.36 | 23.38 | 21.11 | 20.81 | 20.68
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-6B | 20.45 | 20.42 | 20.44 | 20.5 | 20.54 | 22.83 | 23.22 | 23.32 | 23.33 | 21.05 | 20.73 | 20.59
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-6B | 20.67 | 20.64 | 20.66 | 20.69 | 20.71 | 22.96 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.76
SmallHotel | 90.1-2007 | ASHRAE 169-2013-6B | 20.05 | 20.03 | 20.11 | 20.22 | 20.29 | 20.46 | 20.61 | 20.68 | 20.64 | 20.52 | 20.41 | 20.25
SmallOffice | 90.1-2007 | ASHRAE 169-2013-6B | 19.65 | 19.55 | 19.62 | 19.78 | 19.9 | 22.05 | 22.71 | 22.93 | 22.95 | 20.88 | 20.33 | 20
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
Warehouse | 90.1-2007 | ASHRAE 169-2013-6B | 12.48 | 12.49 | 12.53 | 12.6 | 12.63 | 15.67 | 19.39 | 18.82 | 15.11 | 13.08 | 12.79 | 12.63
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-6B | 20.15 | 20.11 | 20.16 | 20.26 | 20.32 | 22.66 | 23.1 | 23.21 | 23.21 | 20.91 | 20.55 | 20.35
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-6B | 20.09 | 20.04 | 20.1 | 20.2 | 20.27 | 22.56 | 23.03 | 23.17 | 23.17 | 20.92 | 20.53 | 20.32
Hospital | 90.1-2010 | ASHRAE 169-2013-6B | 20.56 | 20.54 | 20.56 | 20.6 | 20.63 | 22.84 | 23.25 | 23.34 | 23.36 | 21.14 | 20.81 | 20.68
LargeHotel | 90.1-2010 | ASHRAE 169-2013-6B | 20.1 | 20.07 | 20.13 | 20.22 | 20.29 | 20.43 | 20.56 | 20.63 | 20.6 | 20.51 | 20.41 | 20.27
LargeOffice | 90.1-2010 | ASHRAE 169-2013-6B | 20.55 | 20.52 | 20.55 | 20.59 | 20.62 | 22.84 | 23.24 | 23.34 | 23.35 | 21.13 | 20.8 | 20.67
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6B
MediumOffice | 90.1-2010 | ASHRAE 169-2013-6B | 20.37 | 20.33 | 20.37 | 20.45 | 20.49 | 22.73 | 23.17 | 23.27 | 23.28 | 21.05 | 20.69 | 20.53
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-6B | 20.09 | 20.04 | 20.1 | 20.2 | 20.27 | 22.56 | 23.03 | 23.17 | 23.17 | 20.92 | 20.53 | 20.32
Outpatient | 90.1-2010 | ASHRAE 169-2013-6B | 20.15 | 20.13 | 20.19 | 20.29 | 20.35 | 21.35 | 21.61 | 21.7 | 21.68 | 20.72 | 20.5 | 20.34
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-6B | 20.54 | 20.52 | 20.54 | 20.58 | 20.61 | 22.89 | 23.26 | 23.36 | 23.37 | 21.1 | 20.79 | 20.67
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-6B | 19.79 | 19.75 | 19.83 | 19.97 | 20.07 | 22.46 | 22.95 | 23.1 | 23.08 | 20.75 | 20.35 | 20.08
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-6B | 20.57 | 20.54 | 20.56 | 20.6 | 20.63 | 22.9 | 23.27 | 23.36 | 23.38 | 21.11 | 20.81 | 20.68
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-6B | 20.45 | 20.42 | 20.44 | 20.5 | 20.54 | 22.83 | 23.22 | 23.32 | 23.33 | 21.05 | 20.73 | 20.59
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-6B | 20.67 | 20.64 | 20.66 | 20.69 | 20.71 | 22.96 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.76
SmallHotel | 90.1-2010 | ASHRAE 169-2013-6B | 20.05 | 20.03 | 20.11 | 20.22 | 20.29 | 20.46 | 20.61 | 20.68 | 20.64 | 20.52 | 20.41 | 20.25
SmallOffice | 90.1-2010 | ASHRAE 169-2013-6B | 19.65 | 19.55 | 19.62 | 19.78 | 19.9 | 22.05 | 22.71 | 22.93 | 22.95 | 20.88 | 20.33 | 20
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
Warehouse | 90.1-2010 | ASHRAE 169-2013-6B | 12.48 | 12.49 | 12.53 | 12.6 | 12.63 | 15.67 | 19.39 | 18.82 | 15.11 | 13.08 | 12.79 | 12.63
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-6B | 20.3 | 20.24 | 20.26 | 20.33 | 20.38 | 22.69 | 23.1 | 23.22 | 23.25 | 20.97 | 20.64 | 20.48
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-6B | 20.28 | 20.22 | 20.24 | 20.3 | 20.35 | 22.6 | 23.05 | 23.18 | 23.21 | 20.98 | 20.63 | 20.46
Hospital | 90.1-2013 | ASHRAE 169-2013-6B | 20.62 | 20.58 | 20.59 | 20.63 | 20.65 | 22.85 | 23.25 | 23.34 | 23.37 | 21.16 | 20.84 | 20.73
LargeHotel | 90.1-2013 | ASHRAE 169-2013-6B | 20.18 | 20.14 | 20.18 | 20.26 | 20.31 | 20.44 | 20.56 | 20.63 | 20.61 | 20.54 | 20.46 | 20.34
LargeOffice | 90.1-2013 | ASHRAE 169-2013-6B | 20.61 | 20.57 | 20.58 | 20.62 | 20.64 | 22.84 | 23.24 | 23.34 | 23.37 | 21.15 | 20.84 | 20.72
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6B
MediumOffice | 90.1-2013 | ASHRAE 169-2013-6B | 20.44 | 20.4 | 20.43 | 20.48 | 20.52 | 22.75 | 23.17 | 23.28 | 23.3 | 21.08 | 20.74 | 20.59
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6B | 20.42 | 20.4 | 20.38 | 20.45 | 20.52 | 22.73 | 23.17 | 23.27 | 23.29 | 21.07 | 20.71 | 20.53
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-6B | 20.28 | 20.22 | 20.24 | 20.3 | 20.35 | 22.6 | 23.05 | 23.18 | 23.21 | 20.98 | 20.63 | 20.46
Outpatient | 90.1-2013 | ASHRAE 169-2013-6B | 20.26 | 20.21 | 20.26 | 20.33 | 20.39 | 21.36 | 21.61 | 21.7 | 21.7 | 20.76 | 20.57 | 20.42
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-6B | 20.63 | 20.59 | 20.59 | 20.62 | 20.64 | 22.9 | 23.27 | 23.36 | 23.39 | 21.13 | 20.84 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-6B | 20.02 | 19.94 | 19.98 | 20.07 | 20.15 | 22.5 | 22.96 | 23.11 | 23.13 | 20.83 | 20.47 | 20.26
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-6B | 20.64 | 20.61 | 20.61 | 20.64 | 20.66 | 22.92 | 23.28 | 23.37 | 23.4 | 21.14 | 20.85 | 20.74
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-6B | 20.55 | 20.5 | 20.51 | 20.55 | 20.58 | 22.85 | 23.23 | 23.33 | 23.35 | 21.09 | 20.79 | 20.67
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-6B | 20.73 | 20.69 | 20.69 | 20.71 | 20.73 | 22.97 | 23.32 | 23.41 | 23.44 | 21.18 | 20.9 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2013-6B | 20.16 | 20.12 | 20.18 | 20.27 | 20.33 | 20.47 | 20.6 | 20.67 | 20.65 | 20.56 | 20.47 | 20.33
SmallOffice | 90.1-2013 | ASHRAE 169-2013-6B | 19.84 | 19.71 | 19.75 | 19.86 | 19.97 | 22.08 | 22.71 | 22.94 | 22.99 | 20.95 | 20.43 | 20.14
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-6B | 19.77 | 19.69 | 19.67 | 19.8 | 19.96 | 22.05 | 22.71 | 22.93 | 22.99 | 20.94 | 20.39 | 20.03
Warehouse | 90.1-2013 | ASHRAE 169-2013-6B | 12.48 | 12.49 | 12.53 | 12.6 | 12.63 | 15.67 | 19.39 | 18.82 | 15.11 | 13.08 | 12.79 | 12.63
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-7A | 19.19 | 19.23 | 19.35 | 19.71 | 20.1 | 22.5 | 22.99 | 23.05 | 22.94 | 20.52 | 19.98 | 19.44
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-7A | 19.74 | 19.7 | 19.74 | 19.93 | 20.16 | 22.46 | 22.95 | 23.05 | 23.05 | 20.77 | 20.31 | 19.96
Hospital | 90.1-2004 | ASHRAE 169-2013-7A | 20.22 | 20.22 | 20.26 | 20.4 | 20.56 | 22.79 | 23.21 | 23.27 | 23.26 | 21 | 20.6 | 20.34
LargeHotel | 90.1-2004 | ASHRAE 169-2013-7A | 19.52 | 19.54 | 19.62 | 19.87 | 20.15 | 20.35 | 20.51 | 20.53 | 20.45 | 20.27 | 20.06 | 19.7
LargeOffice | 90.1-2004 | ASHRAE 169-2013-7A | 20.19 | 20.2 | 20.24 | 20.39 | 20.55 | 22.78 | 23.2 | 23.27 | 23.25 | 20.98 | 20.58 | 20.32
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-7A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-7A | 19.84 | 19.85 | 19.92 | 20.14 | 20.38 | 22.65 | 23.11 | 23.17 | 23.13 | 20.83 | 20.37 | 20.01
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-7A | 19.74 | 19.7 | 19.74 | 19.93 | 20.16 | 22.46 | 22.95 | 23.05 | 23.05 | 20.77 | 20.31 | 19.96
Outpatient | 90.1-2004 | ASHRAE 169-2013-7A | 19.45 | 19.49 | 19.59 | 19.89 | 20.2 | 21.25 | 21.55 | 21.58 | 21.5 | 20.44 | 20.08 | 19.65
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-7A | 20.07 | 20.08 | 20.13 | 20.31 | 20.5 | 22.81 | 23.21 | 23.27 | 23.24 | 20.9 | 20.5 | 20.21
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-7A | 18.38 | 18.45 | 18.64 | 19.17 | 19.74 | 22.23 | 22.8 | 22.86 | 22.69 | 20.17 | 19.49 | 18.73
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-7A | 20.11 | 20.12 | 20.17 | 20.34 | 20.52 | 22.82 | 23.22 | 23.28 | 23.25 | 20.92 | 20.53 | 20.25
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-7A | 19.86 | 19.87 | 19.94 | 20.16 | 20.4 | 22.73 | 23.15 | 23.21 | 23.16 | 20.81 | 20.38 | 20.02
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-7A | 20.33 | 20.33 | 20.37 | 20.49 | 20.62 | 22.9 | 23.28 | 23.34 | 23.33 | 21.02 | 20.66 | 20.44
SmallHotel | 90.1-2004 | ASHRAE 169-2013-7A | 19.29 | 19.34 | 19.45 | 19.78 | 20.14 | 20.37 | 20.56 | 20.57 | 20.45 | 20.21 | 19.94 | 19.49
SmallOffice | 90.1-2004 | ASHRAE 169-2013-7A | 18.46 | 18.45 | 18.58 | 19.06 | 19.6 | 21.86 | 22.6 | 22.75 | 22.65 | 20.42 | 19.65 | 18.88
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-7A | 18.67 | 18.5 | 18.73 | 19.07 | 19.43 | 21.75 | 22.5 | 22.67 | 22.56 | 20.4 | 19.65 | 19.05
Warehouse | 90.1-2004 | ASHRAE 169-2013-7A | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-7A | 20.02 | 19.97 | 19.97 | 20.09 | 20.26 | 22.59 | 23.02 | 23.13 | 23.15 | 20.85 | 20.47 | 20.2
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-7A | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Hospital | 90.1-2007 | ASHRAE 169-2013-7A | 20.48 | 20.46 | 20.45 | 20.52 | 20.6 | 22.81 | 23.21 | 23.3 | 23.32 | 21.1 | 20.76 | 20.59
LargeHotel | 90.1-2007 | ASHRAE 169-2013-7A | 19.94 | 19.9 | 19.92 | 20.05 | 20.21 | 20.36 | 20.49 | 20.54 | 20.53 | 20.43 | 20.31 | 20.1
LargeOffice | 90.1-2007 | ASHRAE 169-2013-7A | 20.47 | 20.44 | 20.44 | 20.51 | 20.59 | 22.8 | 23.2 | 23.29 | 23.32 | 21.1 | 20.75 | 20.58
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-7A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-7A | 20.24 | 20.21 | 20.22 | 20.32 | 20.44 | 22.69 | 23.11 | 23.21 | 23.23 | 20.99 | 20.62 | 20.39
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-7A | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Outpatient | 90.1-2007 | ASHRAE 169-2013-7A | 20 | 19.97 | 19.99 | 20.12 | 20.29 | 21.29 | 21.54 | 21.61 | 21.61 | 20.66 | 20.41 | 20.17
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-7A | 20.48 | 20.44 | 20.44 | 20.5 | 20.58 | 22.85 | 23.22 | 23.31 | 23.34 | 21.06 | 20.75 | 20.59
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-7A | 19.61 | 19.55 | 19.56 | 19.74 | 19.98 | 22.37 | 22.85 | 22.98 | 22.99 | 20.66 | 20.23 | 19.87
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-7A | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.87 | 23.23 | 23.32 | 23.35 | 21.08 | 20.77 | 20.61
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-7A | 20.36 | 20.33 | 20.32 | 20.4 | 20.5 | 22.79 | 23.17 | 23.26 | 23.29 | 21.01 | 20.68 | 20.49
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-7A | 20.62 | 20.59 | 20.59 | 20.62 | 20.68 | 22.93 | 23.29 | 23.37 | 23.4 | 21.13 | 20.84 | 20.71
SmallHotel | 90.1-2007 | ASHRAE 169-2013-7A | 19.88 | 19.86 | 19.88 | 20.04 | 20.23 | 20.39 | 20.53 | 20.58 | 20.56 | 20.44 | 20.3 | 20.05
SmallOffice | 90.1-2007 | ASHRAE 169-2013-7A | 19.4 | 19.29 | 19.29 | 19.5 | 19.78 | 21.95 | 22.62 | 22.83 | 22.86 | 20.79 | 20.2 | 19.74
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-7A | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
Warehouse | 90.1-2007 | ASHRAE 169-2013-7A | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-7A | 20.02 | 19.97 | 19.97 | 20.09 | 20.26 | 22.59 | 23.02 | 23.13 | 23.15 | 20.85 | 20.47 | 20.2
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-7A | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Hospital | 90.1-2010 | ASHRAE 169-2013-7A | 20.48 | 20.46 | 20.45 | 20.52 | 20.6 | 22.81 | 23.21 | 23.3 | 23.32 | 21.1 | 20.76 | 20.59
LargeHotel | 90.1-2010 | ASHRAE 169-2013-7A | 19.94 | 19.9 | 19.92 | 20.05 | 20.21 | 20.36 | 20.49 | 20.54 | 20.53 | 20.43 | 20.31 | 20.1
LargeOffice | 90.1-2010 | ASHRAE 169-2013-7A | 20.47 | 20.44 | 20.44 | 20.51 | 20.59 | 22.8 | 23.2 | 23.29 | 23.32 | 21.1 | 20.75 | 20.58
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-7A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-7A | 20.24 | 20.21 | 20.22 | 20.32 | 20.44 | 22.69 | 23.11 | 23.21 | 23.23 | 20.99 | 20.62 | 20.39
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-7A | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Outpatient | 90.1-2010 | ASHRAE 169-2013-7A | 20 | 19.97 | 19.99 | 20.12 | 20.29 | 21.29 | 21.54 | 21.61 | 21.61 | 20.66 | 20.41 | 20.17
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-7A | 20.48 | 20.44 | 20.44 | 20.5 | 20.58 | 22.85 | 23.22 | 23.31 | 23.34 | 21.06 | 20.75 | 20.59
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-7A | 19.61 | 19.55 | 19.56 | 19.74 | 19.98 | 22.37 | 22.85 | 22.98 | 22.99 | 20.66 | 20.23 | 19.87
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-7A | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.87 | 23.23 | 23.32 | 23.35 | 21.08 | 20.77 | 20.61
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-7A | 20.36 | 20.33 | 20.32 | 20.4 | 20.5 | 22.79 | 23.17 | 23.26 | 23.29 | 21.01 | 20.68 | 20.49
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-7A | 20.62 | 20.59 | 20.59 | 20.62 | 20.68 | 22.93 | 23.29 | 23.37 | 23.4 | 21.13 | 20.84 | 20.71
SmallHotel | 90.1-2010 | ASHRAE 169-2013-7A | 19.88 | 19.86 | 19.88 | 20.04 | 20.23 | 20.39 | 20.53 | 20.58 | 20.56 | 20.44 | 20.3 | 20.05
SmallOffice | 90.1-2010 | ASHRAE 169-2013-7A | 19.4 | 19.29 | 19.29 | 19.5 | 19.78 | 21.95 | 22.62 | 22.83 | 22.86 | 20.79 | 20.2 | 19.74
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-7A | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
Warehouse | 90.1-2010 | ASHRAE 169-2013-7A | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-7A | 20.09 | 20.03 | 20.03 | 20.13 | 20.27 | 22.6 | 23.02 | 23.14 | 23.16 | 20.88 | 20.51 | 20.27
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-7A | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
Hospital | 90.1-2013 | ASHRAE 169-2013-7A | 20.51 | 20.48 | 20.47 | 20.53 | 20.61 | 22.81 | 23.21 | 23.3 | 23.33 | 21.11 | 20.78 | 20.62
LargeHotel | 90.1-2013 | ASHRAE 169-2013-7A | 19.97 | 19.94 | 19.95 | 20.06 | 20.22 | 20.36 | 20.48 | 20.54 | 20.53 | 20.45 | 20.33 | 20.13
LargeOffice | 90.1-2013 | ASHRAE 169-2013-7A | 20.49 | 20.46 | 20.46 | 20.52 | 20.59 | 22.81 | 23.21 | 23.3 | 23.32 | 21.11 | 20.77 | 20.61
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-7A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-7A | 20.28 | 20.24 | 20.24 | 20.33 | 20.45 | 22.69 | 23.11 | 23.21 | 23.24 | 21.01 | 20.64 | 20.43
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-7A | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
Outpatient | 90.1-2013 | ASHRAE 169-2013-7A | 20.05 | 20.01 | 20.02 | 20.15 | 20.3 | 21.29 | 21.54 | 21.62 | 21.62 | 20.67 | 20.44 | 20.21
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-7A | 20.52 | 20.48 | 20.47 | 20.52 | 20.59 | 22.86 | 23.22 | 23.31 | 23.34 | 21.08 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-7A | 19.72 | 19.64 | 19.64 | 19.78 | 20 | 22.38 | 22.85 | 22.99 | 23.01 | 20.7 | 20.29 | 19.97
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-7A | 20.54 | 20.5 | 20.49 | 20.54 | 20.61 | 22.87 | 23.24 | 23.32 | 23.36 | 21.09 | 20.79 | 20.64
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-7A | 20.41 | 20.37 | 20.36 | 20.42 | 20.51 | 22.79 | 23.17 | 23.27 | 23.3 | 21.03 | 20.71 | 20.54
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-7A | 20.65 | 20.62 | 20.61 | 20.64 | 20.69 | 22.94 | 23.29 | 23.37 | 23.4 | 21.14 | 20.85 | 20.73
SmallHotel | 90.1-2013 | ASHRAE 169-2013-7A | 19.93 | 19.9 | 19.92 | 20.06 | 20.24 | 20.39 | 20.53 | 20.58 | 20.57 | 20.46 | 20.33 | 20.1
SmallOffice | 90.1-2013 | ASHRAE 169-2013-7A | 19.49 | 19.37 | 19.36 | 19.54 | 19.8 | 21.96 | 22.62 | 22.83 | 22.88 | 20.82 | 20.25 | 19.83
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-7A | 19.57 | 19.38 | 19.42 | 19.56 | 19.75 | 21.9 | 22.56 | 22.78 | 22.82 | 20.8 | 20.24 | 19.85
Warehouse | 90.1-2013 | ASHRAE 169-2013-7A | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-7A | 19.93 | 19.87 | 19.98 | 20.14 | 20.29 | 22.6 | 23.06 | 23.14 | 23.09 | 20.82 | 20.37 | 20.09
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-7A | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-7A | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-7A | 20.32 | 20.24 | 20.27 | 20.34 | 20.42 | 22.66 | 23.09 | 23.19 | 23.21 | 21 | 20.64 | 20.44
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOfficeDetailed | DOE Ref 1980-2004 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-7A | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOfficeDetailed | DOE Ref Pre-1980 | ASHRAE 169-2013-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-7A | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-7B | 19.19 | 19.23 | 19.35 | 19.71 | 20.1 | 22.5 | 22.99 | 23.05 | 22.94 | 20.52 | 19.98 | 19.44
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-7B | 19.74 | 19.7 | 19.74 | 19.93 | 20.16 | 22.46 | 22.95 | 23.05 | 23.05 | 20.77 | 20.31 | 19.96
Hospital | 90.1-2004 | ASHRAE 169-2013-7B | 20.22 | 20.22 | 20.26 | 20.4 | 20.56 | 22.79 | 23.21 | 23.27 | 23.26 | 21 | 20.6 | 20.34
LargeHotel | 90.1-2004 | ASHRAE 169-2013-7B | 19.52 | 19.54 | 19.62 | 19.87 | 20.15 | 20.35 | 20.51 | 20.53 | 20.45 | 20.27 | 20.06 | 19.7
LargeOffice | 90.1-2004 | ASHRAE 169-2013-7B | 20.19 | 20.2 | 20.24 | 20.39 | 20.55 | 22.78 | 23.2 | 23.27 | 23.25 | 20.98 | 20.58 | 20.32
MediumOffice | 90.1-2004 | ASHRAE 169-2013-7B | 19.84 | 19.85 | 19.92 | 20.14 | 20.38 | 22.65 | 23.11 | 23.17 | 23.13 | 20.83 | 20.37 | 20.01
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-7B | 19.74 | 19.7 | 19.74 | 19.93 | 20.16 | 22.46 | 22.95 | 23.05 | 23.05 | 20.77 | 20.31 | 19.96
Outpatient | 90.1-2004 | ASHRAE 169-2013-7B | 19.45 | 19.49 | 19.59 | 19.89 | 20.2 | 21.25 | 21.55 | 21.58 | 21.5 | 20.44 | 20.08 | 19.65
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-7B | 20.07 | 20.08 | 20.13 | 20.31 | 20.5 | 22.81 | 23.21 | 23.27 | 23.24 | 20.9 | 20.5 | 20.21
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-7B | 18.38 | 18.45 | 18.64 | 19.17 | 19.74 | 22.23 | 22.8 | 22.86 | 22.69 | 20.17 | 19.49 | 18.73
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-7B | 20.11 | 20.12 | 20.17 | 20.34 | 20.52 | 22.82 | 23.22 | 23.28 | 23.25 | 20.92 | 20.53 | 20.25
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-7B | 19.86 | 19.87 | 19.94 | 20.16 | 20.4 | 22.73 | 23.15 | 23.21 | 23.16 | 20.81 | 20.38 | 20.02
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-7B | 20.33 | 20.33 | 20.37 | 20.49 | 20.62 | 22.9 | 23.28 | 23.34 | 23.33 | 21.02 | 20.66 | 20.44
SmallHotel | 90.1-2004 | ASHRAE 169-2013-7B | 19.29 | 19.34 | 19.45 | 19.78 | 20.14 | 20.37 | 20.56 | 20.57 | 20.45 | 20.21 | 19.94 | 19.49
SmallOffice | 90.1-2004 | ASHRAE 169-2013-7B | 18.46 | 18.45 | 18.58 | 19.06 | 19.6 | 21.86 | 22.6 | 22.75 | 22.65 | 20.42 | 19.65 | 18.88
Warehouse | 90.1-2004 | ASHRAE 169-2013-7B | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-7B | 20.02 | 19.97 | 19.97 | 20.09 | 20.26 | 22.59 | 23.02 | 23.13 | 23.15 | 20.85 | 20.47 | 20.2
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-7B | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Hospital | 90.1-2007 | ASHRAE 169-2013-7B | 20.48 | 20.46 | 20.45 | 20.52 | 20.6 | 22.81 | 23.21 | 23.3 | 23.32 | 21.1 | 20.76 | 20.59
LargeHotel | 90.1-2007 | ASHRAE 169-2013-7B | 19.94 | 19.9 | 19.92 | 20.05 | 20.21 | 20.36 | 20.49 | 20.54 | 20.53 | 20.43 | 20.31 | 20.1
LargeOffice | 90.1-2007 | ASHRAE 169-2013-7B | 20.47 | 20.44 | 20.44 | 20.51 | 20.59 | 22.8 | 23.2 | 23.29 | 23.32 | 21.1 | 20.75 | 20.58
MediumOffice | 90.1-2007 | ASHRAE 169-2013-7B | 20.24 | 20.21 | 20.22 | 20.32 | 20.44 | 22.69 | 23.11 | 23.21 | 23.23 | 20.99 | 20.62 | 20.39
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-7B | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Outpatient | 90.1-2007 | ASHRAE 169-2013-7B | 20 | 19.97 | 19.99 | 20.12 | 20.29 | 21.29 | 21.54 | 21.61 | 21.61 | 20.66 | 20.41 | 20.17
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-7B | 20.48 | 20.44 | 20.44 | 20.5 | 20.58 | 22.85 | 23.22 | 23.31 | 23.34 | 21.06 | 20.75 | 20.59
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-7B | 19.61 | 19.55 | 19.56 | 19.74 | 19.98 | 22.37 | 22.85 | 22.98 | 22.99 | 20.66 | 20.23 | 19.87
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-7B | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.87 | 23.23 | 23.32 | 23.35 | 21.08 | 20.77 | 20.61
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-7B | 20.36 | 20.33 | 20.32 | 20.4 | 20.5 | 22.79 | 23.17 | 23.26 | 23.29 | 21.01 | 20.68 | 20.49
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-7B | 20.62 | 20.59 | 20.59 | 20.62 | 20.68 | 22.93 | 23.29 | 23.37 | 23.4 | 21.13 | 20.84 | 20.71
SmallHotel | 90.1-2007 | ASHRAE 169-2013-7B | 19.88 | 19.86 | 19.88 | 20.04 | 20.23 | 20.39 | 20.53 | 20.58 | 20.56 | 20.44 | 20.3 | 20.05
SmallOffice | 90.1-2007 | ASHRAE 169-2013-7B | 19.4 | 19.29 | 19.29 | 19.5 | 19.78 | 21.95 | 22.62 | 22.83 | 22.86 | 20.79 | 20.2 | 19.74
Warehouse | 90.1-2007 | ASHRAE 169-2013-7B | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-7B | 20.02 | 19.97 | 19.97 | 20.09 | 20.26 | 22.59 | 23.02 | 23.13 | 23.15 | 20.85 | 20.47 | 20.2
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-7B | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Hospital | 90.1-2010 | ASHRAE 169-2013-7B | 20.48 | 20.46 | 20.45 | 20.52 | 20.6 | 22.81 | 23.21 | 23.3 | 23.32 | 21.1 | 20.76 | 20.59
LargeHotel | 90.1-2010 | ASHRAE 169-2013-7B | 19.94 | 19.9 | 19.92 | 20.05 | 20.21 | 20.36 | 20.49 | 20.54 | 20.53 | 20.43 | 20.31 | 20.1
LargeOffice | 90.1-2010 | ASHRAE 169-2013-7B | 20.47 | 20.44 | 20.44 | 20.51 | 20.59 | 22.8 | 23.2 | 23.29 | 23.32 | 21.1 | 20.75 | 20.58
MediumOffice | 90.1-2010 | ASHRAE 169-2013-7B | 20.24 | 20.21 | 20.22 | 20.32 | 20.44 | 22.69 | 23.11 | 23.21 | 23.23 | 20.99 | 20.62 | 20.39
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-7B | 19.83 | 19.79 | 19.81 | 19.97 | 20.18 | 22.47 | 22.95 | 23.06 | 23.07 | 20.8 | 20.37 | 20.05
Outpatient | 90.1-2010 | ASHRAE 169-2013-7B | 20 | 19.97 | 19.99 | 20.12 | 20.29 | 21.29 | 21.54 | 21.61 | 21.61 | 20.66 | 20.41 | 20.17
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-7B | 20.48 | 20.44 | 20.44 | 20.5 | 20.58 | 22.85 | 23.22 | 23.31 | 23.34 | 21.06 | 20.75 | 20.59
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-7B | 19.61 | 19.55 | 19.56 | 19.74 | 19.98 | 22.37 | 22.85 | 22.98 | 22.99 | 20.66 | 20.23 | 19.87
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-7B | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.87 | 23.23 | 23.32 | 23.35 | 21.08 | 20.77 | 20.61
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-7B | 20.36 | 20.33 | 20.32 | 20.4 | 20.5 | 22.79 | 23.17 | 23.26 | 23.29 | 21.01 | 20.68 | 20.49
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-7B | 20.62 | 20.59 | 20.59 | 20.62 | 20.68 | 22.93 | 23.29 | 23.37 | 23.4 | 21.13 | 20.84 | 20.71
SmallHotel | 90.1-2010 | ASHRAE 169-2013-7B | 19.88 | 19.86 | 19.88 | 20.04 | 20.23 | 20.39 | 20.53 | 20.58 | 20.56 | 20.44 | 20.3 | 20.05
SmallOffice | 90.1-2010 | ASHRAE 169-2013-7B | 19.4 | 19.29 | 19.29 | 19.5 | 19.78 | 21.95 | 22.62 | 22.83 | 22.86 | 20.79 | 20.2 | 19.74
Warehouse | 90.1-2010 | ASHRAE 169-2013-7B | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-7B | 20.09 | 20.03 | 20.03 | 20.13 | 20.27 | 22.6 | 23.02 | 23.14 | 23.16 | 20.88 | 20.51 | 20.27
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-7B | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
Hospital | 90.1-2013 | ASHRAE 169-2013-7B | 20.51 | 20.48 | 20.47 | 20.53 | 20.61 | 22.81 | 23.21 | 23.3 | 23.33 | 21.11 | 20.78 | 20.62
LargeHotel | 90.1-2013 | ASHRAE 169-2013-7B | 19.97 | 19.94 | 19.95 | 20.06 | 20.22 | 20.36 | 20.48 | 20.54 | 20.53 | 20.45 | 20.33 | 20.13
LargeOffice | 90.1-2013 | ASHRAE 169-2013-7B | 20.49 | 20.46 | 20.46 | 20.52 | 20.59 | 22.81 | 23.21 | 23.3 | 23.32 | 21.11 | 20.77 | 20.61
MediumOffice | 90.1-2013 | ASHRAE 169-2013-7B | 20.28 | 20.24 | 20.24 | 20.33 | 20.45 | 22.69 | 23.11 | 23.21 | 23.24 | 21.01 | 20.64 | 20.43
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-7B | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
Outpatient | 90.1-2013 | ASHRAE 169-2013-7B | 20.05 | 20.01 | 20.02 | 20.15 | 20.3 | 21.29 | 21.54 | 21.62 | 21.62 | 20.67 | 20.44 | 20.21
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-7B | 20.52 | 20.48 | 20.47 | 20.52 | 20.59 | 22.86 | 23.22 | 23.31 | 23.34 | 21.08 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-7B | 19.72 | 19.64 | 19.64 | 19.78 | 20 | 22.38 | 22.85 | 22.99 | 23.01 | 20.7 | 20.29 | 19.97
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-7B | 20.54 | 20.5 | 20.49 | 20.54 | 20.61 | 22.87 | 23.24 | 23.32 | 23.36 | 21.09 | 20.79 | 20.64
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-7B | 20.41 | 20.37 | 20.36 | 20.42 | 20.51 | 22.79 | 23.17 | 23.27 | 23.3 | 21.03 | 20.71 | 20.54
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-7B | 20.65 | 20.62 | 20.61 | 20.64 | 20.69 | 22.94 | 23.29 | 23.37 | 23.4 | 21.14 | 20.85 | 20.73
SmallHotel | 90.1-2013 | ASHRAE 169-2013-7B | 19.93 | 19.9 | 19.92 | 20.06 | 20.24 | 20.39 | 20.53 | 20.58 | 20.57 | 20.46 | 20.33 | 20.1
SmallOffice | 90.1-2013 | ASHRAE 169-2013-7B | 19.49 | 19.37 | 19.36 | 19.54 | 19.8 | 21.96 | 22.62 | 22.83 | 22.88 | 20.82 | 20.25 | 19.83
Warehouse | 90.1-2013 | ASHRAE 169-2013-7B | 12.32 | 12.32 | 12.36 | 12.48 | 13.1 | 16.88 | 18.81 | 17.67 | 13.36 | 12.83 | 12.65 | 12.43
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-8A | 19.55 | 19.52 | 19.55 | 19.73 | 20 | 22.39 | 22.82 | 22.94 | 22.9 | 20.55 | 19.97 | 19.66
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-8A | 19.46 | 19.43 | 19.46 | 19.65 | 19.93 | 22.27 | 22.75 | 22.88 | 22.85 | 20.54 | 19.92 | 19.57
Hospital | 90.1-2004 | ASHRAE 169-2013-8A | 20.29 | 20.27 | 20.28 | 20.36 | 20.49 | 22.72 | 23.12 | 23.21 | 23.21 | 20.97 | 20.54 | 20.36
LargeHotel | 90.1-2004 | ASHRAE 169-2013-8A | 19.56 | 19.55 | 19.58 | 19.74 | 19.99 | 20.18 | 20.31 | 20.38 | 20.32 | 20.18 | 19.89 | 19.64
LargeOffice | 90.1-2004 | ASHRAE 169-2013-8A | 20.27 | 20.25 | 20.25 | 20.34 | 20.47 | 22.71 | 23.11 | 23.2 | 23.2 | 20.96 | 20.52 | 20.34
LargeOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-8A
MediumOffice | 90.1-2004 | ASHRAE 169-2013-8A | 19.95 | 19.93 | 19.95 | 20.08 | 20.27 | 22.55 | 22.98 | 23.08 | 23.06 | 20.79 | 20.28 | 20.04
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-8A | 19.46 | 19.43 | 19.46 | 19.65 | 19.93 | 22.27 | 22.75 | 22.88 | 22.85 | 20.54 | 19.92 | 19.57
Outpatient | 90.1-2004 | ASHRAE 169-2013-8A | 19.62 | 19.61 | 19.64 | 19.82 | 20.07 | 21.11 | 21.37 | 21.45 | 21.39 | 20.39 | 19.97 | 19.7
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-8A | 20.24 | 20.21 | 20.22 | 20.31 | 20.44 | 22.74 | 23.12 | 23.21 | 23.21 | 20.91 | 20.49 | 20.31
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-8A | 18.94 | 18.91 | 18.96 | 19.23 | 19.61 | 22.08 | 22.57 | 22.72 | 22.65 | 20.24 | 19.51 | 19.09
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-8A | 20.27 | 20.25 | 20.26 | 20.34 | 20.47 | 22.76 | 23.13 | 23.22 | 23.22 | 20.93 | 20.52 | 20.34
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-8A | 20.07 | 20.05 | 20.06 | 20.17 | 20.34 | 22.66 | 23.04 | 23.14 | 23.13 | 20.82 | 20.36 | 20.15
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-8A | 20.45 | 20.43 | 20.43 | 20.49 | 20.58 | 22.86 | 23.21 | 23.3 | 23.3 | 21.02 | 20.65 | 20.51
SmallHotel | 90.1-2004 | ASHRAE 169-2013-8A | 19.46 | 19.46 | 19.5 | 19.7 | 19.99 | 20.2 | 20.34 | 20.41 | 20.33 | 20.15 | 19.81 | 19.54
SmallOffice | 90.1-2004 | ASHRAE 169-2013-8A | 18.75 | 18.67 | 18.69 | 18.97 | 19.41 | 21.67 | 22.34 | 22.57 | 22.53 | 20.38 | 19.52 | 18.99
SmallOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-8A | 18.59 | 18.4 | 18.47 | 18.75 | 19.2 | 21.51 | 22.24 | 22.47 | 22.45 | 20.31 | 19.46 | 18.99
Warehouse | 90.1-2004 | ASHRAE 169-2013-8A | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-8A | 19.68 | 19.64 | 19.66 | 19.8 | 20.03 | 22.41 | 22.84 | 22.96 | 22.95 | 20.62 | 20.09 | 19.8
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-8A | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Hospital | 90.1-2007 | ASHRAE 169-2013-8A | 20.33 | 20.31 | 20.31 | 20.38 | 20.5 | 22.73 | 23.12 | 23.22 | 23.23 | 20.99 | 20.57 | 20.4
LargeHotel | 90.1-2007 | ASHRAE 169-2013-8A | 19.62 | 19.61 | 19.63 | 19.78 | 20 | 20.18 | 20.31 | 20.38 | 20.34 | 20.21 | 19.95 | 19.7
LargeOffice | 90.1-2007 | ASHRAE 169-2013-8A | 20.31 | 20.28 | 20.29 | 20.36 | 20.48 | 22.71 | 23.11 | 23.21 | 23.22 | 20.98 | 20.56 | 20.38
LargeOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-8A
MediumOffice | 90.1-2007 | ASHRAE 169-2013-8A | 20.01 | 19.99 | 20 | 20.11 | 20.29 | 22.56 | 22.98 | 23.09 | 23.09 | 20.83 | 20.33 | 20.1
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-8A | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Outpatient | 90.1-2007 | ASHRAE 169-2013-8A | 19.7 | 19.68 | 19.7 | 19.86 | 20.09 | 21.12 | 21.38 | 21.46 | 21.42 | 20.44 | 20.04 | 19.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-8A | 20.3 | 20.27 | 20.27 | 20.35 | 20.46 | 22.75 | 23.13 | 23.22 | 23.23 | 20.94 | 20.55 | 20.38
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-8A | 19.13 | 19.08 | 19.11 | 19.33 | 19.66 | 22.11 | 22.59 | 22.75 | 22.71 | 20.34 | 19.69 | 19.28
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-8A | 20.34 | 20.31 | 20.31 | 20.38 | 20.48 | 22.77 | 23.14 | 23.24 | 23.25 | 20.96 | 20.58 | 20.41
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-8A | 20.15 | 20.12 | 20.12 | 20.21 | 20.36 | 22.67 | 23.05 | 23.16 | 23.16 | 20.87 | 20.44 | 20.24
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-8A | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.86 | 23.22 | 23.3 | 23.32 | 21.05 | 20.7 | 20.56
SmallHotel | 90.1-2007 | ASHRAE 169-2013-8A | 19.55 | 19.54 | 19.57 | 19.75 | 20.01 | 20.21 | 20.35 | 20.42 | 20.36 | 20.2 | 19.89 | 19.63
SmallOffice | 90.1-2007 | ASHRAE 169-2013-8A | 18.89 | 18.8 | 18.81 | 19.06 | 19.45 | 21.69 | 22.36 | 22.59 | 22.58 | 20.46 | 19.65 | 19.13
SmallOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-8A | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
Warehouse | 90.1-2007 | ASHRAE 169-2013-8A | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-8A | 19.68 | 19.64 | 19.66 | 19.8 | 20.03 | 22.41 | 22.84 | 22.96 | 22.95 | 20.62 | 20.09 | 19.8
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-8A | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Hospital | 90.1-2010 | ASHRAE 169-2013-8A | 20.33 | 20.31 | 20.31 | 20.38 | 20.5 | 22.73 | 23.12 | 23.22 | 23.23 | 20.99 | 20.57 | 20.4
LargeHotel | 90.1-2010 | ASHRAE 169-2013-8A | 19.62 | 19.61 | 19.63 | 19.78 | 20 | 20.18 | 20.31 | 20.38 | 20.34 | 20.21 | 19.95 | 19.7
LargeOffice | 90.1-2010 | ASHRAE 169-2013-8A | 20.31 | 20.28 | 20.29 | 20.36 | 20.48 | 22.71 | 23.11 | 23.21 | 23.22 | 20.98 | 20.56 | 20.38
LargeOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-8A
MediumOffice | 90.1-2010 | ASHRAE 169-2013-8A | 20.01 | 19.99 | 20 | 20.11 | 20.29 | 22.56 | 22.98 | 23.09 | 23.09 | 20.83 | 20.33 | 20.1
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-8A | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Outpatient | 90.1-2010 | ASHRAE 169-2013-8A | 19.7 | 19.68 | 19.7 | 19.86 | 20.09 | 21.12 | 21.38 | 21.46 | 21.42 | 20.44 | 20.04 | 19.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-8A | 20.3 | 20.27 | 20.27 | 20.35 | 20.46 | 22.75 | 23.13 | 23.22 | 23.23 | 20.94 | 20.55 | 20.38
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-8A | 19.13 | 19.08 | 19.11 | 19.33 | 19.66 | 22.11 | 22.59 | 22.75 | 22.71 | 20.34 | 19.69 | 19.28
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-8A | 20.34 | 20.31 | 20.31 | 20.38 | 20.48 | 22.77 | 23.14 | 23.24 | 23.25 | 20.96 | 20.58 | 20.41
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-8A | 20.15 | 20.12 | 20.12 | 20.21 | 20.36 | 22.67 | 23.05 | 23.16 | 23.16 | 20.87 | 20.44 | 20.24
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-8A | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.86 | 23.22 | 23.3 | 23.32 | 21.05 | 20.7 | 20.56
SmallHotel | 90.1-2010 | ASHRAE 169-2013-8A | 19.55 | 19.54 | 19.57 | 19.75 | 20.01 | 20.21 | 20.35 | 20.42 | 20.36 | 20.2 | 19.89 | 19.63
SmallOffice | 90.1-2010 | ASHRAE 169-2013-8A | 18.89 | 18.8 | 18.81 | 19.06 | 19.45 | 21.69 | 22.36 | 22.59 | 22.58 | 20.46 | 19.65 | 19.13
SmallOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-8A | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
Warehouse | 90.1-2010 | ASHRAE 169-2013-8A | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-8A | 19.76 | 19.72 | 19.72 | 19.85 | 20.05 | 22.42 | 22.84 | 22.98 | 22.98 | 20.67 | 20.16 | 19.88
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-8A | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
Hospital | 90.1-2013 | ASHRAE 169-2013-8A | 20.44 | 20.41 | 20.41 | 20.45 | 20.53 | 22.75 | 23.14 | 23.24 | 23.26 | 21.05 | 20.67 | 20.52
LargeHotel | 90.1-2013 | ASHRAE 169-2013-8A | 19.84 | 19.81 | 19.81 | 19.91 | 20.08 | 20.22 | 20.33 | 20.4 | 20.39 | 20.31 | 20.12 | 19.93
LargeOffice | 90.1-2013 | ASHRAE 169-2013-8A | 20.43 | 20.39 | 20.39 | 20.44 | 20.52 | 22.74 | 23.13 | 23.23 | 23.25 | 21.04 | 20.65 | 20.5
LargeOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-8A
MediumOffice | 90.1-2013 | ASHRAE 169-2013-8A | 20.18 | 20.15 | 20.14 | 20.22 | 20.34 | 22.59 | 23.01 | 23.12 | 23.14 | 20.91 | 20.47 | 20.27
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-8A | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
Outpatient | 90.1-2013 | ASHRAE 169-2013-8A | 19.91 | 19.88 | 19.88 | 19.99 | 20.16 | 21.16 | 21.4 | 21.49 | 21.48 | 20.54 | 20.21 | 20
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-8A | 20.34 | 20.31 | 20.31 | 20.37 | 20.47 | 22.76 | 23.13 | 23.23 | 23.25 | 20.97 | 20.59 | 20.42
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-8A | 19.24 | 19.19 | 19.2 | 19.39 | 19.69 | 22.13 | 22.6 | 22.77 | 22.75 | 20.41 | 19.79 | 19.41
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-8A | 20.38 | 20.35 | 20.34 | 20.4 | 20.49 | 22.78 | 23.15 | 23.24 | 23.26 | 20.99 | 20.61 | 20.45
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-8A | 20.2 | 20.17 | 20.17 | 20.24 | 20.37 | 22.68 | 23.06 | 23.17 | 23.18 | 20.89 | 20.48 | 20.29
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-8A | 20.53 | 20.5 | 20.49 | 20.53 | 20.6 | 22.87 | 23.22 | 23.31 | 23.33 | 21.06 | 20.72 | 20.59
SmallHotel | 90.1-2013 | ASHRAE 169-2013-8A | 19.79 | 19.77 | 19.78 | 19.9 | 20.09 | 20.25 | 20.37 | 20.44 | 20.42 | 20.32 | 20.09 | 19.88
SmallOffice | 90.1-2013 | ASHRAE 169-2013-8A | 18.98 | 18.88 | 18.89 | 19.11 | 19.47 | 21.7 | 22.37 | 22.61 | 22.62 | 20.51 | 19.73 | 19.23
SmallOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-8A | 18.84 | 18.64 | 18.67 | 18.89 | 19.27 | 21.55 | 22.26 | 22.51 | 22.54 | 20.45 | 19.66 | 19.22
Warehouse | 90.1-2013 | ASHRAE 169-2013-8A | 12.35 | 12.34 | 12.34 | 12.41 | 12.51 | 15.14 | 16.26 | 14.27 | 12.88 | 12.67 | 12.52 | 12.4
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOfficeDetailed | 90.1-2004 | ASHRAE 169-2013-8A | 19.87 | 19.79 | 19.85 | 19.98 | 20.18 | 22.48 | 22.93 | 23.03 | 23.02 | 20.76 | 20.24 | 20.04
MediumOfficeDetailed | 90.1-2007 | ASHRAE 169-2013-8A | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MediumOfficeDetailed | 90.1-2010 | ASHRAE 169-2013-8A | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MediumOfficeDetailed | 90.1-2013 | ASHRAE 169-2013-8A | 20.12 | 20.04 | 20.06 | 20.13 | 20.27 | 22.53 | 22.96 | 23.08 | 23.1 | 20.88 | 20.44 | 20.27
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2013-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2013-8A | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2013-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2013-8A | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-8B | 19.55 | 19.52 | 19.55 | 19.73 | 20 | 22.39 | 22.82 | 22.94 | 22.9 | 20.55 | 19.97 | 19.66
HighriseApartment | 90.1-2004 | ASHRAE 169-2013-8B | 19.46 | 19.43 | 19.46 | 19.65 | 19.93 | 22.27 | 22.75 | 22.88 | 22.85 | 20.54 | 19.92 | 19.57
Hospital | 90.1-2004 | ASHRAE 169-2013-8B | 20.29 | 20.27 | 20.28 | 20.36 | 20.49 | 22.72 | 23.12 | 23.21 | 23.21 | 20.97 | 20.54 | 20.36
LargeHotel | 90.1-2004 | ASHRAE 169-2013-8B | 19.56 | 19.55 | 19.58 | 19.74 | 19.99 | 20.18 | 20.31 | 20.38 | 20.32 | 20.18 | 19.89 | 19.64
LargeOffice | 90.1-2004 | ASHRAE 169-2013-8B | 20.27 | 20.25 | 20.25 | 20.34 | 20.47 | 22.71 | 23.11 | 23.2 | 23.2 | 20.96 | 20.52 | 20.34
MediumOffice | 90.1-2004 | ASHRAE 169-2013-8B | 19.95 | 19.93 | 19.95 | 20.08 | 20.27 | 22.55 | 22.98 | 23.08 | 23.06 | 20.79 | 20.28 | 20.04
MidriseApartment | 90.1-2004 | ASHRAE 169-2013-8B | 19.46 | 19.43 | 19.46 | 19.65 | 19.93 | 22.27 | 22.75 | 22.88 | 22.85 | 20.54 | 19.92 | 19.57
Outpatient | 90.1-2004 | ASHRAE 169-2013-8B | 19.62 | 19.61 | 19.64 | 19.82 | 20.07 | 21.11 | 21.37 | 21.45 | 21.39 | 20.39 | 19.97 | 19.7
PrimarySchool | 90.1-2004 | ASHRAE 169-2013-8B | 20.24 | 20.21 | 20.22 | 20.31 | 20.44 | 22.74 | 23.12 | 23.21 | 23.21 | 20.91 | 20.49 | 20.31
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2013-8B | 18.94 | 18.91 | 18.96 | 19.23 | 19.61 | 22.08 | 22.57 | 22.72 | 22.65 | 20.24 | 19.51 | 19.09
RetailStandalone | 90.1-2004 | ASHRAE 169-2013-8B | 20.27 | 20.25 | 20.26 | 20.34 | 20.47 | 22.76 | 23.13 | 23.22 | 23.22 | 20.93 | 20.52 | 20.34
RetailStripmall | 90.1-2004 | ASHRAE 169-2013-8B | 20.07 | 20.05 | 20.06 | 20.17 | 20.34 | 22.66 | 23.04 | 23.14 | 23.13 | 20.82 | 20.36 | 20.15
SecondarySchool | 90.1-2004 | ASHRAE 169-2013-8B | 20.45 | 20.43 | 20.43 | 20.49 | 20.58 | 22.86 | 23.21 | 23.3 | 23.3 | 21.02 | 20.65 | 20.51
SmallHotel | 90.1-2004 | ASHRAE 169-2013-8B | 19.46 | 19.46 | 19.5 | 19.7 | 19.99 | 20.2 | 20.34 | 20.41 | 20.33 | 20.15 | 19.81 | 19.54
SmallOffice | 90.1-2004 | ASHRAE 169-2013-8B | 18.75 | 18.67 | 18.69 | 18.97 | 19.41 | 21.67 | 22.34 | 22.57 | 22.53 | 20.38 | 19.52 | 18.99
Warehouse | 90.1-2004 | ASHRAE 169-2013-8B | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-8B | 19.68 | 19.64 | 19.66 | 19.8 | 20.03 | 22.41 | 22.84 | 22.96 | 22.95 | 20.62 | 20.09 | 19.8
HighriseApartment | 90.1-2007 | ASHRAE 169-2013-8B | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Hospital | 90.1-2007 | ASHRAE 169-2013-8B | 20.33 | 20.31 | 20.31 | 20.38 | 20.5 | 22.73 | 23.12 | 23.22 | 23.23 | 20.99 | 20.57 | 20.4
LargeHotel | 90.1-2007 | ASHRAE 169-2013-8B | 19.62 | 19.61 | 19.63 | 19.78 | 20 | 20.18 | 20.31 | 20.38 | 20.34 | 20.21 | 19.95 | 19.7
LargeOffice | 90.1-2007 | ASHRAE 169-2013-8B | 20.31 | 20.28 | 20.29 | 20.36 | 20.48 | 22.71 | 23.11 | 23.21 | 23.22 | 20.98 | 20.56 | 20.38
MediumOffice | 90.1-2007 | ASHRAE 169-2013-8B | 20.01 | 19.99 | 20 | 20.11 | 20.29 | 22.56 | 22.98 | 23.09 | 23.09 | 20.83 | 20.33 | 20.1
MidriseApartment | 90.1-2007 | ASHRAE 169-2013-8B | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Outpatient | 90.1-2007 | ASHRAE 169-2013-8B | 19.7 | 19.68 | 19.7 | 19.86 | 20.09 | 21.12 | 21.38 | 21.46 | 21.42 | 20.44 | 20.04 | 19.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2013-8B | 20.3 | 20.27 | 20.27 | 20.35 | 20.46 | 22.75 | 23.13 | 23.22 | 23.23 | 20.94 | 20.55 | 20.38
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2013-8B | 19.13 | 19.08 | 19.11 | 19.33 | 19.66 | 22.11 | 22.59 | 22.75 | 22.71 | 20.34 | 19.69 | 19.28
RetailStandalone | 90.1-2007 | ASHRAE 169-2013-8B | 20.34 | 20.31 | 20.31 | 20.38 | 20.48 | 22.77 | 23.14 | 23.24 | 23.25 | 20.96 | 20.58 | 20.41
RetailStripmall | 90.1-2007 | ASHRAE 169-2013-8B | 20.15 | 20.12 | 20.12 | 20.21 | 20.36 | 22.67 | 23.05 | 23.16 | 23.16 | 20.87 | 20.44 | 20.24
SecondarySchool | 90.1-2007 | ASHRAE 169-2013-8B | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.86 | 23.22 | 23.3 | 23.32 | 21.05 | 20.7 | 20.56
SmallHotel | 90.1-2007 | ASHRAE 169-2013-8B | 19.55 | 19.54 | 19.57 | 19.75 | 20.01 | 20.21 | 20.35 | 20.42 | 20.36 | 20.2 | 19.89 | 19.63
SmallOffice | 90.1-2007 | ASHRAE 169-2013-8B | 18.89 | 18.8 | 18.81 | 19.06 | 19.45 | 21.69 | 22.36 | 22.59 | 22.58 | 20.46 | 19.65 | 19.13
Warehouse | 90.1-2007 | ASHRAE 169-2013-8B | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-8B | 19.68 | 19.64 | 19.66 | 19.8 | 20.03 | 22.41 | 22.84 | 22.96 | 22.95 | 20.62 | 20.09 | 19.8
HighriseApartment | 90.1-2010 | ASHRAE 169-2013-8B | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Hospital | 90.1-2010 | ASHRAE 169-2013-8B | 20.33 | 20.31 | 20.31 | 20.38 | 20.5 | 22.73 | 23.12 | 23.22 | 23.23 | 20.99 | 20.57 | 20.4
LargeHotel | 90.1-2010 | ASHRAE 169-2013-8B | 19.62 | 19.61 | 19.63 | 19.78 | 20 | 20.18 | 20.31 | 20.38 | 20.34 | 20.21 | 19.95 | 19.7
LargeOffice | 90.1-2010 | ASHRAE 169-2013-8B | 20.31 | 20.28 | 20.29 | 20.36 | 20.48 | 22.71 | 23.11 | 23.21 | 23.22 | 20.98 | 20.56 | 20.38
MediumOffice | 90.1-2010 | ASHRAE 169-2013-8B | 20.01 | 19.99 | 20 | 20.11 | 20.29 | 22.56 | 22.98 | 23.09 | 23.09 | 20.83 | 20.33 | 20.1
MidriseApartment | 90.1-2010 | ASHRAE 169-2013-8B | 19.52 | 19.49 | 19.51 | 19.68 | 19.95 | 22.28 | 22.75 | 22.89 | 22.87 | 20.58 | 19.98 | 19.64
Outpatient | 90.1-2010 | ASHRAE 169-2013-8B | 19.7 | 19.68 | 19.7 | 19.86 | 20.09 | 21.12 | 21.38 | 21.46 | 21.42 | 20.44 | 20.04 | 19.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2013-8B | 20.3 | 20.27 | 20.27 | 20.35 | 20.46 | 22.75 | 23.13 | 23.22 | 23.23 | 20.94 | 20.55 | 20.38
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2013-8B | 19.13 | 19.08 | 19.11 | 19.33 | 19.66 | 22.11 | 22.59 | 22.75 | 22.71 | 20.34 | 19.69 | 19.28
RetailStandalone | 90.1-2010 | ASHRAE 169-2013-8B | 20.34 | 20.31 | 20.31 | 20.38 | 20.48 | 22.77 | 23.14 | 23.24 | 23.25 | 20.96 | 20.58 | 20.41
RetailStripmall | 90.1-2010 | ASHRAE 169-2013-8B | 20.15 | 20.12 | 20.12 | 20.21 | 20.36 | 22.67 | 23.05 | 23.16 | 23.16 | 20.87 | 20.44 | 20.24
SecondarySchool | 90.1-2010 | ASHRAE 169-2013-8B | 20.5 | 20.47 | 20.47 | 20.52 | 20.6 | 22.86 | 23.22 | 23.3 | 23.32 | 21.05 | 20.7 | 20.56
SmallHotel | 90.1-2010 | ASHRAE 169-2013-8B | 19.55 | 19.54 | 19.57 | 19.75 | 20.01 | 20.21 | 20.35 | 20.42 | 20.36 | 20.2 | 19.89 | 19.63
SmallOffice | 90.1-2010 | ASHRAE 169-2013-8B | 18.89 | 18.8 | 18.81 | 19.06 | 19.45 | 21.69 | 22.36 | 22.59 | 22.58 | 20.46 | 19.65 | 19.13
Warehouse | 90.1-2010 | ASHRAE 169-2013-8B | 12.14 | 12.14 | 12.18 | 12.32 | 12.5 | 15.15 | 16.27 | 14.28 | 12.85 | 12.57 | 12.32 | 12.17
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-8B | 19.76 | 19.72 | 19.72 | 19.85 | 20.05 | 22.42 | 22.84 | 22.98 | 22.98 | 20.67 | 20.16 | 19.88
HighriseApartment | 90.1-2013 | ASHRAE 169-2013-8B | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
Hospital | 90.1-2013 | ASHRAE 169-2013-8B | 20.44 | 20.41 | 20.41 | 20.45 | 20.53 | 22.75 | 23.14 | 23.24 | 23.26 | 21.05 | 20.67 | 20.52
LargeHotel | 90.1-2013 | ASHRAE 169-2013-8B | 19.84 | 19.81 | 19.81 | 19.91 | 20.08 | 20.22 | 20.33 | 20.4 | 20.39 | 20.31 | 20.12 | 19.93
LargeOffice | 90.1-2013 | ASHRAE 169-2013-8B | 20.43 | 20.39 | 20.39 | 20.44 | 20.52 | 22.74 | 23.13 | 23.23 | 23.25 | 21.04 | 20.65 | 20.5
MediumOffice | 90.1-2013 | ASHRAE 169-2013-8B | 20.18 | 20.15 | 20.14 | 20.22 | 20.34 | 22.59 | 23.01 | 23.12 | 23.14 | 20.91 | 20.47 | 20.27
MidriseApartment | 90.1-2013 | ASHRAE 169-2013-8B | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
Outpatient | 90.1-2013 | ASHRAE 169-2013-8B | 19.91 | 19.88 | 19.88 | 19.99 | 20.16 | 21.16 | 21.4 | 21.49 | 21.48 | 20.54 | 20.21 | 20
PrimarySchool | 90.1-2013 | ASHRAE 169-2013-8B | 20.34 | 20.31 | 20.31 | 20.37 | 20.47 | 22.76 | 23.13 | 23.23 | 23.25 | 20.97 | 20.59 | 20.42
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2013-8B | 19.24 | 19.19 | 19.2 | 19.39 | 19.69 | 22.13 | 22.6 | 22.77 | 22.75 | 20.41 | 19.79 | 19.41
RetailStandalone | 90.1-2013 | ASHRAE 169-2013-8B | 20.38 | 20.35 | 20.34 | 20.4 | 20.49 | 22.78 | 23.15 | 23.24 | 23.26 | 20.99 | 20.61 | 20.45
RetailStripmall | 90.1-2013 | ASHRAE 169-2013-8B | 20.2 | 20.17 | 20.17 | 20.24 | 20.37 | 22.68 | 23.06 | 23.17 | 23.18 | 20.89 | 20.48 | 20.29
SecondarySchool | 90.1-2013 | ASHRAE 169-2013-8B | 20.53 | 20.5 | 20.49 | 20.53 | 20.6 | 22.87 | 23.22 | 23.31 | 23.33 | 21.06 | 20.72 | 20.59
SmallHotel | 90.1-2013 | ASHRAE 169-2013-8B | 19.79 | 19.77 | 19.78 | 19.9 | 20.09 | 20.25 | 20.37 | 20.44 | 20.42 | 20.32 | 20.09 | 19.88
SmallOffice | 90.1-2013 | ASHRAE 169-2013-8B | 18.98 | 18.88 | 18.89 | 19.11 | 19.47 | 21.7 | 22.37 | 22.61 | 22.62 | 20.51 | 19.73 | 19.23
Warehouse | 90.1-2013 | ASHRAE 169-2013-8B | 12.35 | 12.34 | 12.34 | 12.41 | 12.51 | 15.14 | 16.26 | 14.27 | 12.88 | 12.67 | 12.52 | 12.4
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2004 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2004 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2004 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2004 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2004 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2004 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2007 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2007 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2007 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2007 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2007 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2007 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2010 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2010 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2010 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2010 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2010 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2010 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 21 | 21.03 | 21.11 | 21.16 | 23.38 | 23.69 | 23.76 | 23.76 | 21.49 | 21.21 | 21.07
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Hospital | 90.1-2013 | ASHRAE 169-2006-1A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
LargeOffice | 90.1-2013 | ASHRAE 169-2006-1A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.04 | 21.06 | 23.22 | 23.57 | 23.64 | 23.66 | 21.46 | 21.16 | 21.05
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
Outpatient | 90.1-2013 | ASHRAE 169-2006-1A | 20.96 | 20.96 | 20.99 | 21.06 | 21.1 | 21.99 | 22.14 | 22.18 | 22.17 | 21.28 | 21.11 | 21.01
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.05 | 23.26 | 23.58 | 23.64 | 23.66 | 21.4 | 21.14 | 21.05
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1A | 21.01 | 21.01 | 21.06 | 21.19 | 21.26 | 23.48 | 23.8 | 23.87 | 23.85 | 21.58 | 21.27 | 21.1
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.99 | 21.03 | 21.04 | 23.26 | 23.57 | 23.64 | 23.66 | 21.4 | 21.13 | 21.04
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-1A | 20.99 | 20.98 | 20.98 | 21 | 21.02 | 23.23 | 23.54 | 23.61 | 23.63 | 21.37 | 21.12 | 21.04
SmallHotel | 90.1-2013 | ASHRAE 169-2006-1A | 20.94 | 20.95 | 20.99 | 21.07 | 21.11 | 21.16 | 21.19 | 21.21 | 21.18 | 21.14 | 21.08 | 20.99
SmallOffice | 90.1-2013 | ASHRAE 169-2006-1A | 20.96 | 20.94 | 20.97 | 21.09 | 21.16 | 23.13 | 23.6 | 23.73 | 23.75 | 21.75 | 21.3 | 21.09
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-1A | 21 | 20.99 | 21 | 21.05 | 21.08 | 23.29 | 23.61 | 23.67 | 23.69 | 21.42 | 21.16 | 21.05
Warehouse | 90.1-2013 | ASHRAE 169-2006-1A | 20.19 | 20.72 | 21.39 | 23.77 | 25.14 | 26.54 | 27.33 | 27.4 | 26.65 | 25.11 | 23.37 | 20.99
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 22.509 | 22.645 | 22.781 | 22.956 | 23.052 | 23.08 | 23.116 | 23.108 | 23.133 | 23.139 | 23.077 | 22.913
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-1A | 10.7 | 10.54 | 11.61 | 13.26 | 16.58 | 19.47 | 22.27 | 24.29 | 21.8 | 17.54 | 14.44 | 11.6
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2004 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2004 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2004 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2004 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2004 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2004 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2007 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2007 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2007 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2007 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2007 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2007 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2010 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2010 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2010 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2010 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2010 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2010 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.64 | 23.98 | 24.09 | 24.07 | 21.71 | 21.29 | 21.01
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Hospital | 90.1-2013 | ASHRAE 169-2006-1B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
LargeOffice | 90.1-2013 | ASHRAE 169-2006-1B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.95 | 21.05 | 21.16 | 23.39 | 23.75 | 23.85 | 23.86 | 21.6 | 21.22 | 21.02
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
Outpatient | 90.1-2013 | ASHRAE 169-2006-1B | 20.85 | 20.87 | 20.94 | 21.07 | 21.23 | 22.21 | 22.38 | 22.46 | 22.44 | 21.47 | 21.2 | 20.97
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-1B | 20.92 | 20.92 | 20.96 | 21.03 | 21.13 | 23.4 | 23.72 | 23.81 | 23.82 | 21.51 | 21.18 | 21.02
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-1B | 20.79 | 20.83 | 20.96 | 21.19 | 21.48 | 23.87 | 24.21 | 24.34 | 24.3 | 21.9 | 21.39 | 21
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-1B | 20.93 | 20.92 | 20.96 | 21.03 | 21.12 | 23.39 | 23.71 | 23.79 | 23.81 | 21.5 | 21.18 | 21.02
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-1B | 20.94 | 20.93 | 20.96 | 21.01 | 21.07 | 23.33 | 23.64 | 23.72 | 23.74 | 21.45 | 21.15 | 21.02
SmallHotel | 90.1-2013 | ASHRAE 169-2006-1B | 20.82 | 20.85 | 20.93 | 21.08 | 21.26 | 21.41 | 21.45 | 21.51 | 21.47 | 21.35 | 21.17 | 20.94
SmallOffice | 90.1-2013 | ASHRAE 169-2006-1B | 20.78 | 20.76 | 20.87 | 21.08 | 21.36 | 23.5 | 24.02 | 24.21 | 24.22 | 22.1 | 21.48 | 21.05
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-1B | 20.91 | 20.91 | 20.96 | 21.05 | 21.17 | 23.46 | 23.78 | 23.88 | 23.88 | 21.56 | 21.21 | 21.02
Warehouse | 90.1-2013 | ASHRAE 169-2006-1B | 14.79 | 16.72 | 19.78 | 24.59 | 30.22 | 33.53 | 34.88 | 35.37 | 32.81 | 28.11 | 22.6 | 16.33
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2004 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2004 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2004 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2004 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2004 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2007 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2007 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2007 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2007 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2007 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2010 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2010 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2010 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2010 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2010 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2A | 20.59 | 20.53 | 20.67 | 20.8 | 20.96 | 23.24 | 23.6 | 23.68 | 23.67 | 21.35 | 20.98 | 20.69
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Hospital | 90.1-2013 | ASHRAE 169-2006-2A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-2A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-2A | 20.73 | 20.68 | 20.76 | 20.84 | 20.94 | 23.13 | 23.5 | 23.58 | 23.6 | 21.36 | 21.01 | 20.81
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
Outpatient | 90.1-2013 | ASHRAE 169-2006-2A | 20.62 | 20.57 | 20.68 | 20.8 | 20.93 | 21.87 | 22.06 | 22.11 | 22.1 | 21.15 | 20.91 | 20.69
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-2A | 20.78 | 20.74 | 20.81 | 20.87 | 20.95 | 23.19 | 23.53 | 23.6 | 23.61 | 21.33 | 21.02 | 20.85
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2A | 20.41 | 20.33 | 20.54 | 20.74 | 20.98 | 23.29 | 23.67 | 23.76 | 23.73 | 21.38 | 20.94 | 20.54
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-2A | 20.79 | 20.75 | 20.81 | 20.87 | 20.95 | 23.19 | 23.52 | 23.59 | 23.61 | 21.33 | 21.02 | 20.86
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-2A | 20.84 | 20.81 | 20.85 | 20.89 | 20.94 | 23.18 | 23.51 | 23.57 | 23.6 | 21.32 | 21.03 | 20.9
SmallHotel | 90.1-2013 | ASHRAE 169-2006-2A | 20.56 | 20.52 | 20.65 | 20.78 | 20.93 | 21.04 | 21.11 | 21.13 | 21.1 | 21 | 20.86 | 20.64
SmallOffice | 90.1-2013 | ASHRAE 169-2006-2A | 20.38 | 20.28 | 20.43 | 20.62 | 20.85 | 22.92 | 23.46 | 23.6 | 23.62 | 21.54 | 20.98 | 20.57
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-2A | 20.74 | 20.69 | 20.77 | 20.85 | 20.95 | 23.2 | 23.54 | 23.62 | 23.63 | 21.33 | 21.01 | 20.81
Warehouse | 90.1-2013 | ASHRAE 169-2006-2A | 13.19 | 13.04 | 15.76 | 19.5 | 22.75 | 25.31 | 26.94 | 26.7 | 25.13 | 21.35 | 17.77 | 13.7
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 20.541 | 20.346 | 20.801 | 22.127 | 22.752 | 22.868 | 22.937 | 22.96 | 22.981 | 22.822 | 21.631 | 20.645
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-2A | 10.61 | 10.45 | 11.54 | 13.27 | 16.58 | 19.44 | 22.24 | 24.28 | 21.77 | 17.49 | 14.43 | 11.56
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2004 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2004 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2004 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2004 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2004 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2004 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2007 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2007 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2007 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2007 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2007 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2007 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2010 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2010 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2010 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2010 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2010 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2010 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.66 | 20.81 | 20.97 | 21.11 | 23.49 | 23.9 | 23.96 | 23.93 | 21.53 | 21.11 | 20.79
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Hospital | 90.1-2013 | ASHRAE 169-2006-2B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
LargeOffice | 90.1-2013 | ASHRAE 169-2006-2B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-2B | 20.78 | 20.76 | 20.85 | 20.95 | 21.03 | 23.29 | 23.69 | 23.76 | 23.76 | 21.48 | 21.09 | 20.87
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
Outpatient | 90.1-2013 | ASHRAE 169-2006-2B | 20.68 | 20.68 | 20.8 | 20.94 | 21.05 | 22.07 | 22.31 | 22.34 | 22.31 | 21.3 | 21.03 | 20.78
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-2B | 20.83 | 20.81 | 20.88 | 20.96 | 21.03 | 23.32 | 23.68 | 23.74 | 23.75 | 21.42 | 21.09 | 20.9
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-2B | 20.52 | 20.51 | 20.74 | 20.98 | 21.19 | 23.65 | 24.1 | 24.16 | 24.11 | 21.63 | 21.12 | 20.69
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-2B | 20.83 | 20.82 | 20.88 | 20.96 | 21.02 | 23.31 | 23.67 | 23.73 | 23.74 | 21.42 | 21.09 | 20.91
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-2B | 20.87 | 20.86 | 20.9 | 20.95 | 21 | 23.27 | 23.61 | 23.68 | 23.69 | 21.39 | 21.08 | 20.94
SmallHotel | 90.1-2013 | ASHRAE 169-2006-2B | 20.64 | 20.64 | 20.78 | 20.93 | 21.07 | 21.26 | 21.37 | 21.38 | 21.33 | 21.17 | 20.98 | 20.73
SmallOffice | 90.1-2013 | ASHRAE 169-2006-2B | 20.48 | 20.44 | 20.6 | 20.84 | 21.04 | 23.23 | 23.85 | 23.99 | 23.98 | 21.81 | 21.17 | 20.72
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-2B | 20.79 | 20.78 | 20.86 | 20.96 | 21.05 | 23.36 | 23.73 | 23.79 | 23.79 | 21.45 | 21.09 | 20.88
Warehouse | 90.1-2013 | ASHRAE 169-2006-2B | 13.33 | 13.17 | 17.7 | 20.9 | 24.62 | 30.29 | 31.97 | 31.6 | 29.42 | 23.49 | 18.35 | 13.91
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 19.266 | 19.196 | 20.396 | 21.375 | 21.525 | 21.18 | 21.067 | 21.286 | 21.442 | 21.586 | 20.307 | 19.387
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-2B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2004 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2004 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2004 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2007 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2007 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2007 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Hospital | 90.1-2010 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3A | 20.28 | 20.25 | 20.39 | 20.59 | 20.82 | 23.07 | 23.5 | 23.59 | 23.55 | 21.21 | 20.75 | 20.45
Outpatient | 90.1-2010 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2010 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3A | 20.28 | 20.26 | 20.41 | 20.61 | 20.83 | 23.15 | 23.54 | 23.63 | 23.58 | 21.18 | 20.75 | 20.45
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
Hospital | 90.1-2013 | ASHRAE 169-2006-3A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3A | 20.53 | 20.51 | 20.6 | 20.72 | 20.85 | 23.07 | 23.47 | 23.55 | 23.54 | 21.25 | 20.86 | 20.65
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
Outpatient | 90.1-2013 | ASHRAE 169-2006-3A | 20.36 | 20.35 | 20.47 | 20.64 | 20.82 | 21.79 | 22.02 | 22.07 | 22.02 | 21 | 20.72 | 20.49
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3A | 20.63 | 20.6 | 20.67 | 20.77 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.9 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3A | 19.96 | 19.93 | 20.16 | 20.46 | 20.79 | 23.16 | 23.6 | 23.69 | 23.6 | 21.13 | 20.61 | 20.19
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3A | 20.64 | 20.62 | 20.69 | 20.78 | 20.88 | 23.14 | 23.5 | 23.57 | 23.57 | 21.24 | 20.91 | 20.74
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3A | 20.73 | 20.71 | 20.75 | 20.82 | 20.89 | 23.14 | 23.48 | 23.56 | 23.56 | 21.26 | 20.95 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3A | 20.29 | 20.27 | 20.42 | 20.6 | 20.81 | 20.95 | 21.06 | 21.09 | 21.02 | 20.83 | 20.65 | 20.42
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3A | 19.96 | 19.9 | 20.07 | 20.34 | 20.66 | 22.79 | 23.38 | 23.54 | 23.51 | 21.31 | 20.68 | 20.24
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3A | 20.55 | 20.52 | 20.61 | 20.73 | 20.87 | 23.14 | 23.51 | 23.58 | 23.57 | 21.23 | 20.87 | 20.66
Warehouse | 90.1-2013 | ASHRAE 169-2006-3A | 12.94 | 12.86 | 12.86 | 16.47 | 21.05 | 24.57 | 26.19 | 26.03 | 23.11 | 17.55 | 13.67 | 13.12
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 19.963 | 19.905 | 19.939 | 20.453 | 22.043 | 22.528 | 22.672 | 22.78 | 22.808 | 21.178 | 20.28 | 20.042
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3A | 10.51 | 10.33 | 11.44 | 13.16 | 16.48 | 19.37 | 22.18 | 24.28 | 21.77 | 17.43 | 14.32 | 11.46
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2004 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2004 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2004 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2007 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2007 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2007 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Hospital | 90.1-2010 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3B | 20.41 | 20.42 | 20.56 | 20.65 | 20.87 | 23.19 | 23.62 | 23.66 | 23.62 | 21.32 | 20.81 | 20.56
Outpatient | 90.1-2010 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2010 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3B | 20.41 | 20.43 | 20.57 | 20.67 | 20.88 | 23.27 | 23.66 | 23.69 | 23.65 | 21.29 | 20.81 | 20.56
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
Hospital | 90.1-2013 | ASHRAE 169-2006-3B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3B | 20.62 | 20.61 | 20.7 | 20.75 | 20.89 | 23.14 | 23.54 | 23.59 | 23.58 | 21.32 | 20.9 | 20.72
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
Outpatient | 90.1-2013 | ASHRAE 169-2006-3B | 20.47 | 20.48 | 20.6 | 20.69 | 20.86 | 21.89 | 22.11 | 22.12 | 22.08 | 21.1 | 20.77 | 20.58
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3B | 20.69 | 20.69 | 20.76 | 20.8 | 20.91 | 23.2 | 23.56 | 23.61 | 23.6 | 21.3 | 20.93 | 20.78
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3B | 20.15 | 20.18 | 20.4 | 20.55 | 20.87 | 23.33 | 23.76 | 23.78 | 23.7 | 21.28 | 20.69 | 20.35
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3B | 20.71 | 20.71 | 20.77 | 20.81 | 20.91 | 23.2 | 23.55 | 23.6 | 23.6 | 21.3 | 20.94 | 20.79
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3B | 20.78 | 20.77 | 20.81 | 20.84 | 20.91 | 23.19 | 23.53 | 23.58 | 23.59 | 21.3 | 20.97 | 20.85
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3B | 20.4 | 20.43 | 20.56 | 20.66 | 20.86 | 21.06 | 21.16 | 21.14 | 21.08 | 20.94 | 20.7 | 20.52
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3B | 20.13 | 20.1 | 20.29 | 20.43 | 20.73 | 22.94 | 23.54 | 23.63 | 23.6 | 21.46 | 20.77 | 20.38
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3B | 20.63 | 20.63 | 20.71 | 20.77 | 20.9 | 23.22 | 23.58 | 23.63 | 23.61 | 21.29 | 20.91 | 20.73
Warehouse | 90.1-2013 | ASHRAE 169-2006-3B | 13 | 12.93 | 13.51 | 16.19 | 21.28 | 26.23 | 27.17 | 25.64 | 23.19 | 18.61 | 13.81 | 13.19
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 18.89 | 18.889 | 18.895 | 20.344 | 20.899 | 20.929 | 20.753 | 20.826 | 21.013 | 20.868 | 19.246 | 18.923
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2004 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2004 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2004 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2004 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2004 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2004 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2007 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2007 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2007 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2007 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2007 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2007 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Hospital | 90.1-2010 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2010 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-3C | 20.32 | 20.37 | 20.36 | 20.43 | 20.49 | 22.64 | 23.02 | 23.09 | 23.13 | 20.98 | 20.61 | 20.42
Outpatient | 90.1-2010 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2010 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2010 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2010 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3C | 20.33 | 20.37 | 20.38 | 20.44 | 20.51 | 22.71 | 23.07 | 23.13 | 23.16 | 20.95 | 20.61 | 20.42
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
Hospital | 90.1-2013 | ASHRAE 169-2006-3C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
LargeOffice | 90.1-2013 | ASHRAE 169-2006-3C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-3C | 20.56 | 20.58 | 20.57 | 20.61 | 20.65 | 22.79 | 23.17 | 23.23 | 23.27 | 21.11 | 20.77 | 20.63
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
Outpatient | 90.1-2013 | ASHRAE 169-2006-3C | 20.4 | 20.44 | 20.44 | 20.5 | 20.55 | 21.44 | 21.63 | 21.66 | 21.68 | 20.8 | 20.6 | 20.47
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-3C | 20.65 | 20.66 | 20.66 | 20.68 | 20.72 | 22.92 | 23.26 | 23.32 | 23.35 | 21.12 | 20.83 | 20.71
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-3C | 20.04 | 20.11 | 20.12 | 20.22 | 20.33 | 22.53 | 22.9 | 22.96 | 22.99 | 20.8 | 20.4 | 20.16
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-3C | 20.66 | 20.68 | 20.67 | 20.7 | 20.73 | 22.93 | 23.27 | 23.33 | 23.36 | 21.13 | 20.84 | 20.72
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-3C | 20.74 | 20.75 | 20.74 | 20.76 | 20.78 | 22.98 | 23.31 | 23.37 | 23.41 | 21.18 | 20.89 | 20.8
SmallHotel | 90.1-2013 | ASHRAE 169-2006-3C | 20.33 | 20.38 | 20.39 | 20.45 | 20.51 | 20.57 | 20.64 | 20.64 | 20.65 | 20.61 | 20.52 | 20.39
SmallOffice | 90.1-2013 | ASHRAE 169-2006-3C | 20.04 | 20.07 | 20.07 | 20.15 | 20.24 | 22.19 | 22.71 | 22.82 | 22.88 | 20.95 | 20.47 | 20.19
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-3C | 20.57 | 20.59 | 20.59 | 20.63 | 20.67 | 22.87 | 23.21 | 23.27 | 23.31 | 21.08 | 20.77 | 20.64
Warehouse | 90.1-2013 | ASHRAE 169-2006-3C | 12.76 | 12.76 | 12.75 | 12.76 | 13.58 | 14.42 | 15.67 | 15.85 | 16.37 | 15.08 | 13.09 | 12.83
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 19.905 | 19.922 | 19.91 | 19.932 | 19.949 | 20.038 | 20.327 | 20.062 | 20.443 | 20.088 | 19.986 | 19.948
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-3C | 10.56 | 10.42 | 11.49 | 13.19 | 16.48 | 19.37 | 22.14 | 24.19 | 21.68 | 17.4 | 14.34 | 11.52
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4A | 19.99 | 19.92 | 20.1 | 20.24 | 20.48 | 22.81 | 23.29 | 23.4 | 23.33 | 21.03 | 20.52 | 20.17
Hospital | 90.1-2004 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4A | 19.99 | 19.92 | 20.1 | 20.24 | 20.48 | 22.81 | 23.29 | 23.4 | 23.33 | 21.03 | 20.52 | 20.17
Outpatient | 90.1-2004 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2004 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Hospital | 90.1-2007 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Outpatient | 90.1-2007 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2007 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4A | 20 | 19.93 | 20.11 | 20.26 | 20.49 | 22.89 | 23.33 | 23.44 | 23.36 | 21 | 20.52 | 20.17
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Hospital | 90.1-2010 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4A | 20.35 | 20.3 | 20.41 | 20.49 | 20.64 | 22.9 | 23.33 | 23.43 | 23.4 | 21.14 | 20.72 | 20.48
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4A | 20.31 | 20.22 | 20.3 | 20.38 | 20.51 | 22.79 | 23.24 | 23.36 | 23.36 | 21.12 | 20.71 | 20.46
Outpatient | 90.1-2010 | ASHRAE 169-2006-4A | 20.12 | 20.07 | 20.22 | 20.34 | 20.54 | 21.58 | 21.84 | 21.91 | 21.84 | 20.85 | 20.53 | 20.26
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4A | 20.48 | 20.43 | 20.52 | 20.59 | 20.71 | 23.01 | 23.39 | 23.47 | 23.45 | 21.15 | 20.79 | 20.58
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4A | 19.55 | 19.46 | 19.73 | 19.96 | 20.31 | 22.79 | 23.29 | 23.42 | 23.29 | 20.87 | 20.28 | 19.79
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4A | 20.5 | 20.46 | 20.54 | 20.61 | 20.72 | 23.01 | 23.39 | 23.47 | 23.46 | 21.16 | 20.8 | 20.61
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4A | 20.03 | 19.97 | 20.15 | 20.28 | 20.5 | 20.73 | 20.87 | 20.92 | 20.83 | 20.66 | 20.44 | 20.17
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4A | 19.58 | 19.45 | 19.66 | 19.86 | 20.19 | 22.4 | 23.07 | 23.28 | 23.21 | 21.07 | 20.38 | 19.87
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4A | 20.36 | 20.31 | 20.42 | 20.51 | 20.65 | 22.98 | 23.37 | 23.46 | 23.43 | 21.11 | 20.72 | 20.49
Warehouse | 90.1-2010 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4A | 20.47 | 20.39 | 20.42 | 20.48 | 20.57 | 22.88 | 23.27 | 23.39 | 23.41 | 21.13 | 20.79 | 20.6
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
Hospital | 90.1-2013 | ASHRAE 169-2006-4A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4A | 20.62 | 20.59 | 20.64 | 20.69 | 20.77 | 23.05 | 23.41 | 23.48 | 23.48 | 21.19 | 20.87 | 20.71
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4A | 20.58 | 20.52 | 20.55 | 20.59 | 20.67 | 22.89 | 23.29 | 23.4 | 23.42 | 21.21 | 20.85 | 20.69
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
Outpatient | 90.1-2013 | ASHRAE 169-2006-4A | 20.44 | 20.37 | 20.42 | 20.48 | 20.58 | 21.54 | 21.78 | 21.86 | 21.85 | 20.94 | 20.71 | 20.55
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4A | 20.71 | 20.66 | 20.68 | 20.7 | 20.74 | 23 | 23.36 | 23.45 | 23.47 | 21.21 | 20.92 | 20.8
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4A | 20.25 | 20.15 | 20.2 | 20.28 | 20.42 | 22.77 | 23.2 | 23.34 | 23.36 | 21.07 | 20.68 | 20.43
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4A | 20.73 | 20.68 | 20.69 | 20.71 | 20.75 | 23.01 | 23.36 | 23.45 | 23.48 | 21.22 | 20.92 | 20.81
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4A | 20.79 | 20.75 | 20.75 | 20.77 | 20.8 | 23.04 | 23.38 | 23.47 | 23.5 | 21.24 | 20.96 | 20.86
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4A | 20.36 | 20.3 | 20.36 | 20.43 | 20.54 | 20.67 | 20.78 | 20.85 | 20.83 | 20.75 | 20.63 | 20.48
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4A | 20.11 | 19.97 | 20.01 | 20.1 | 20.27 | 22.38 | 22.99 | 23.2 | 23.25 | 21.22 | 20.67 | 20.35
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4A | 20.65 | 20.6 | 20.61 | 20.64 | 20.7 | 22.97 | 23.34 | 23.43 | 23.46 | 21.19 | 20.89 | 20.75
Warehouse | 90.1-2013 | ASHRAE 169-2006-4A | 12.74 | 12.67 | 12.7 | 12.74 | 16.14 | 21 | 23.32 | 23.64 | 19.96 | 14.91 | 13.22 | 12.88
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 19.713 | 19.665 | 19.706 | 19.745 | 20.486 | 22.11 | 22.459 | 22.554 | 22.169 | 20.607 | 20.047 | 19.805
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4A | 10.41 | 10.24 | 11.37 | 13.1 | 16.43 | 19.37 | 22.17 | 24.22 | 21.68 | 17.38 | 14.27 | 11.38
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4B | 20.1 | 20.13 | 20.21 | 20.39 | 20.64 | 22.94 | 23.41 | 23.5 | 23.43 | 21.11 | 20.54 | 20.25
Hospital | 90.1-2004 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4B | 20.1 | 20.13 | 20.21 | 20.39 | 20.64 | 22.94 | 23.41 | 23.5 | 23.43 | 21.11 | 20.54 | 20.25
Outpatient | 90.1-2004 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2004 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Hospital | 90.1-2007 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Outpatient | 90.1-2007 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2007 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4B | 20.11 | 20.14 | 20.23 | 20.4 | 20.65 | 23.01 | 23.46 | 23.53 | 23.47 | 21.08 | 20.54 | 20.25
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Hospital | 90.1-2010 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4B | 20.42 | 20.43 | 20.48 | 20.59 | 20.74 | 22.98 | 23.41 | 23.49 | 23.46 | 21.19 | 20.73 | 20.53
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4B | 20.38 | 20.36 | 20.4 | 20.48 | 20.63 | 22.89 | 23.33 | 23.44 | 23.44 | 21.19 | 20.74 | 20.52
Outpatient | 90.1-2010 | ASHRAE 169-2006-4B | 20.21 | 20.24 | 20.32 | 20.47 | 20.67 | 21.68 | 21.94 | 21.99 | 21.93 | 20.92 | 20.55 | 20.33
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4B | 20.54 | 20.54 | 20.58 | 20.66 | 20.79 | 23.07 | 23.45 | 23.52 | 23.51 | 21.19 | 20.8 | 20.63
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4B | 19.71 | 19.77 | 19.9 | 20.17 | 20.54 | 22.97 | 23.47 | 23.55 | 23.44 | 20.99 | 20.3 | 19.91
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4B | 20.56 | 20.56 | 20.6 | 20.68 | 20.79 | 23.08 | 23.45 | 23.52 | 23.51 | 21.2 | 20.81 | 20.65
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4B | 20.12 | 20.17 | 20.25 | 20.42 | 20.65 | 20.84 | 20.98 | 21 | 20.92 | 20.74 | 20.46 | 20.24
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4B | 19.71 | 19.71 | 19.82 | 20.06 | 20.41 | 22.58 | 23.24 | 23.4 | 23.34 | 21.19 | 20.41 | 19.97
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4B | 20.43 | 20.45 | 20.5 | 20.6 | 20.75 | 23.06 | 23.45 | 23.52 | 23.5 | 21.17 | 20.74 | 20.54
Warehouse | 90.1-2010 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4B | 20.53 | 20.5 | 20.51 | 20.56 | 20.66 | 22.96 | 23.36 | 23.46 | 23.48 | 21.19 | 20.82 | 20.65
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
Hospital | 90.1-2013 | ASHRAE 169-2006-4B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4B | 20.67 | 20.66 | 20.69 | 20.74 | 20.83 | 23.09 | 23.45 | 23.52 | 23.52 | 21.22 | 20.87 | 20.74
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4B | 20.63 | 20.6 | 20.61 | 20.65 | 20.73 | 22.95 | 23.35 | 23.45 | 23.47 | 21.25 | 20.88 | 20.73
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
Outpatient | 90.1-2013 | ASHRAE 169-2006-4B | 20.49 | 20.48 | 20.5 | 20.56 | 20.66 | 21.62 | 21.85 | 21.92 | 21.91 | 20.99 | 20.74 | 20.59
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4B | 20.75 | 20.72 | 20.72 | 20.74 | 20.79 | 23.05 | 23.4 | 23.49 | 23.51 | 21.25 | 20.94 | 20.82
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4B | 20.34 | 20.3 | 20.32 | 20.4 | 20.55 | 22.89 | 23.32 | 23.44 | 23.45 | 21.15 | 20.73 | 20.5
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4B | 20.76 | 20.73 | 20.73 | 20.75 | 20.8 | 23.05 | 23.4 | 23.49 | 23.51 | 21.25 | 20.94 | 20.83
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4B | 20.81 | 20.79 | 20.79 | 20.8 | 20.83 | 23.07 | 23.42 | 23.49 | 23.52 | 21.26 | 20.97 | 20.88
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4B | 20.42 | 20.41 | 20.45 | 20.51 | 20.64 | 20.76 | 20.87 | 20.91 | 20.89 | 20.82 | 20.67 | 20.53
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4B | 20.19 | 20.12 | 20.14 | 20.23 | 20.41 | 22.51 | 23.11 | 23.3 | 23.34 | 21.3 | 20.73 | 20.41
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4B | 20.69 | 20.67 | 20.67 | 20.7 | 20.76 | 23.03 | 23.39 | 23.48 | 23.5 | 21.23 | 20.91 | 20.78
Warehouse | 90.1-2013 | ASHRAE 169-2006-4B | 12.78 | 12.75 | 12.75 | 12.8 | 17.63 | 21.41 | 24.22 | 23.02 | 20.59 | 14.35 | 13.17 | 12.91
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 19.213 | 19.212 | 19.191 | 19.196 | 20.446 | 21.39 | 21.565 | 21.74 | 21.83 | 19.836 | 19.374 | 19.272
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4B | 10.35 | 10.21 | 11.27 | 12.93 | 16.14 | 18.94 | 21.69 | 23.84 | 21.43 | 17.17 | 14.11 | 11.29
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-4C | 20.06 | 20.07 | 20.12 | 20.2 | 20.36 | 22.6 | 23.05 | 23.18 | 23.15 | 20.86 | 20.38 | 20.21
Hospital | 90.1-2004 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2004 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-4C | 20.06 | 20.07 | 20.12 | 20.2 | 20.36 | 22.6 | 23.05 | 23.18 | 23.15 | 20.86 | 20.38 | 20.21
Outpatient | 90.1-2004 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2004 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2004 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2004 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Hospital | 90.1-2007 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2007 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Outpatient | 90.1-2007 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2007 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2007 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2007 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4C | 20.07 | 20.09 | 20.13 | 20.22 | 20.37 | 22.68 | 23.1 | 23.22 | 23.19 | 20.84 | 20.38 | 20.21
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Hospital | 90.1-2010 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2010 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-4C | 20.4 | 20.4 | 20.42 | 20.47 | 20.56 | 22.77 | 23.18 | 23.29 | 23.28 | 21.03 | 20.63 | 20.5
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-4C | 20.32 | 20.31 | 20.32 | 20.36 | 20.45 | 22.67 | 23.08 | 23.2 | 23.22 | 20.99 | 20.59 | 20.44
Outpatient | 90.1-2010 | ASHRAE 169-2006-4C | 20.18 | 20.2 | 20.24 | 20.31 | 20.44 | 21.41 | 21.65 | 21.73 | 21.7 | 20.71 | 20.41 | 20.29
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-4C | 20.51 | 20.51 | 20.53 | 20.57 | 20.65 | 22.9 | 23.27 | 23.36 | 23.36 | 21.07 | 20.71 | 20.6
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-4C | 19.65 | 19.69 | 19.77 | 19.9 | 20.13 | 22.49 | 22.95 | 23.1 | 23.03 | 20.63 | 20.08 | 19.86
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-4C | 20.54 | 20.54 | 20.55 | 20.59 | 20.66 | 22.92 | 23.28 | 23.37 | 23.37 | 21.08 | 20.73 | 20.62
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
SmallHotel | 90.1-2010 | ASHRAE 169-2006-4C | 20.09 | 20.12 | 20.17 | 20.25 | 20.39 | 20.54 | 20.66 | 20.72 | 20.67 | 20.51 | 20.31 | 20.2
SmallOffice | 90.1-2010 | ASHRAE 169-2006-4C | 19.67 | 19.66 | 19.72 | 19.82 | 20.04 | 22.13 | 22.74 | 22.94 | 22.94 | 20.82 | 20.17 | 19.9
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-4C | 20.41 | 20.41 | 20.44 | 20.48 | 20.58 | 22.85 | 23.23 | 23.32 | 23.32 | 21.01 | 20.63 | 20.51
Warehouse | 90.1-2010 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4C | 20.47 | 20.44 | 20.44 | 20.46 | 20.52 | 22.79 | 23.16 | 23.27 | 23.3 | 21.03 | 20.69 | 20.57
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
Hospital | 90.1-2013 | ASHRAE 169-2006-4C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-4C | 20.65 | 20.64 | 20.65 | 20.68 | 20.73 | 22.97 | 23.32 | 23.4 | 23.42 | 21.13 | 20.81 | 20.72
LargeOffice | 90.1-2013 | ASHRAE 169-2006-4C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-4C | 20.59 | 20.57 | 20.57 | 20.58 | 20.63 | 22.82 | 23.2 | 23.31 | 23.34 | 21.13 | 20.78 | 20.67
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
Outpatient | 90.1-2013 | ASHRAE 169-2006-4C | 20.44 | 20.43 | 20.44 | 20.46 | 20.53 | 21.46 | 21.66 | 21.74 | 21.75 | 20.83 | 20.62 | 20.53
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-4C | 20.71 | 20.69 | 20.69 | 20.69 | 20.72 | 22.96 | 23.3 | 23.38 | 23.42 | 21.16 | 20.87 | 20.78
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-4C | 20.25 | 20.22 | 20.23 | 20.26 | 20.35 | 22.64 | 23.04 | 23.17 | 23.2 | 20.92 | 20.54 | 20.39
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-4C | 20.73 | 20.7 | 20.7 | 20.7 | 20.73 | 22.97 | 23.3 | 23.39 | 23.42 | 21.17 | 20.88 | 20.79
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-4C | 20.79 | 20.77 | 20.76 | 20.76 | 20.78 | 23.01 | 23.34 | 23.42 | 23.46 | 21.2 | 20.92 | 20.85
SmallHotel | 90.1-2013 | ASHRAE 169-2006-4C | 20.37 | 20.36 | 20.38 | 20.41 | 20.49 | 20.58 | 20.66 | 20.71 | 20.71 | 20.64 | 20.53 | 20.45
SmallOffice | 90.1-2013 | ASHRAE 169-2006-4C | 20.11 | 20.06 | 20.06 | 20.1 | 20.21 | 22.24 | 22.8 | 22.99 | 23.05 | 21.04 | 20.51 | 20.29
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-4C | 20.65 | 20.63 | 20.63 | 20.64 | 20.67 | 22.92 | 23.26 | 23.35 | 23.39 | 21.13 | 20.82 | 20.73
Warehouse | 90.1-2013 | ASHRAE 169-2006-4C | 12.66 | 12.65 | 12.66 | 12.68 | 12.9 | 15.26 | 17.68 | 18.6 | 16.67 | 13.27 | 12.86 | 12.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 19.744 | 19.735 | 19.741 | 19.771 | 19.825 | 20.04 | 20.738 | 21.085 | 20.449 | 19.986 | 19.848 | 19.775
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-4C | 10.49 | 10.34 | 11.42 | 13.14 | 16.46 | 19.35 | 22.13 | 24.18 | 21.65 | 17.37 | 14.28 | 11.43
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5A | 19.76 | 19.73 | 19.83 | 20.06 | 20.32 | 22.7 | 23.19 | 23.26 | 23.22 | 20.87 | 20.35 | 19.99
Hospital | 90.1-2004 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5A | 19.76 | 19.73 | 19.83 | 20.06 | 20.32 | 22.7 | 23.19 | 23.26 | 23.22 | 20.87 | 20.35 | 19.99
Outpatient | 90.1-2004 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2004 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2007 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5A | 19.77 | 19.74 | 19.84 | 20.08 | 20.34 | 22.78 | 23.24 | 23.3 | 23.25 | 20.85 | 20.35 | 19.99
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5A | 20.21 | 20.18 | 20.24 | 20.38 | 20.54 | 22.83 | 23.27 | 23.33 | 23.33 | 21.04 | 20.61 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5A | 20.14 | 20.08 | 20.11 | 20.23 | 20.39 | 22.7 | 23.15 | 23.25 | 23.27 | 21.01 | 20.59 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2006-5A | 19.93 | 19.91 | 20 | 20.19 | 20.41 | 21.49 | 21.76 | 21.79 | 21.75 | 20.71 | 20.39 | 20.11
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5A | 20.36 | 20.34 | 20.38 | 20.5 | 20.63 | 22.95 | 23.34 | 23.4 | 23.39 | 21.07 | 20.7 | 20.49
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5A | 19.22 | 19.18 | 19.34 | 19.7 | 20.09 | 22.64 | 23.16 | 23.21 | 23.13 | 20.64 | 20.04 | 19.53
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5A | 20.39 | 20.37 | 20.41 | 20.52 | 20.64 | 22.96 | 23.34 | 23.4 | 23.4 | 21.08 | 20.72 | 20.52
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5A | 19.82 | 19.8 | 19.9 | 20.12 | 20.36 | 20.63 | 20.78 | 20.79 | 20.73 | 20.51 | 20.29 | 20
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5A | 19.27 | 19.18 | 19.29 | 19.59 | 19.96 | 22.25 | 22.94 | 23.08 | 23.06 | 20.85 | 20.16 | 19.63
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5A | 20.22 | 20.19 | 20.25 | 20.4 | 20.56 | 22.91 | 23.31 | 23.37 | 23.36 | 21.02 | 20.62 | 20.37
Warehouse | 90.1-2010 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5A | 20.34 | 20.27 | 20.28 | 20.35 | 20.46 | 22.79 | 23.2 | 23.3 | 23.33 | 21.05 | 20.69 | 20.5
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
Hospital | 90.1-2013 | ASHRAE 169-2006-5A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5A | 20.54 | 20.52 | 20.55 | 20.63 | 20.72 | 23.01 | 23.37 | 23.43 | 23.44 | 21.14 | 20.8 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5A | 20.49 | 20.43 | 20.44 | 20.5 | 20.59 | 22.83 | 23.24 | 23.33 | 23.36 | 21.14 | 20.78 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
Outpatient | 90.1-2013 | ASHRAE 169-2006-5A | 20.31 | 20.26 | 20.28 | 20.36 | 20.48 | 21.47 | 21.71 | 21.77 | 21.78 | 20.84 | 20.62 | 20.45
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5A | 20.65 | 20.6 | 20.6 | 20.64 | 20.69 | 22.96 | 23.32 | 23.4 | 23.43 | 21.17 | 20.87 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5A | 20.07 | 19.98 | 19.99 | 20.11 | 20.26 | 22.65 | 23.1 | 23.22 | 23.25 | 20.94 | 20.55 | 20.28
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5A | 20.66 | 20.62 | 20.62 | 20.65 | 20.7 | 22.97 | 23.33 | 23.41 | 23.44 | 21.17 | 20.88 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5A | 20.74 | 20.71 | 20.7 | 20.72 | 20.76 | 23.01 | 23.36 | 23.43 | 23.47 | 21.21 | 20.92 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5A | 20.23 | 20.17 | 20.2 | 20.3 | 20.43 | 20.59 | 20.71 | 20.75 | 20.75 | 20.65 | 20.54 | 20.37
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5A | 19.91 | 19.78 | 19.78 | 19.91 | 20.1 | 22.25 | 22.88 | 23.07 | 23.13 | 21.08 | 20.53 | 20.19
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5A | 20.57 | 20.52 | 20.52 | 20.57 | 20.63 | 22.92 | 23.29 | 23.38 | 23.41 | 21.14 | 20.82 | 20.68
Warehouse | 90.1-2013 | ASHRAE 169-2006-5A | 12.61 | 12.57 | 12.58 | 12.65 | 14.73 | 19.66 | 22.3 | 21.36 | 18.32 | 13.55 | 12.97 | 12.75
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 19.527 | 19.502 | 19.536 | 19.598 | 20.002 | 21.64 | 22.225 | 22.375 | 21.449 | 20.121 | 19.802 | 19.633
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-5A | 10.34 | 10.19 | 11.31 | 13.07 | 16.39 | 19.3 | 22.1 | 24.2 | 21.69 | 17.32 | 14.23 | 11.34
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5B | 19.84 | 19.94 | 20 | 20.15 | 20.37 | 22.67 | 23.25 | 23.33 | 23.2 | 20.87 | 20.3 | 19.98
Hospital | 90.1-2004 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5B | 19.84 | 19.94 | 20 | 20.15 | 20.37 | 22.67 | 23.25 | 23.33 | 23.2 | 20.87 | 20.3 | 19.98
Outpatient | 90.1-2004 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2004 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Hospital | 90.1-2007 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Outpatient | 90.1-2007 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2007 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5B | 19.85 | 19.95 | 20.01 | 20.17 | 20.39 | 22.75 | 23.29 | 23.36 | 23.24 | 20.84 | 20.31 | 19.98
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Hospital | 90.1-2010 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5B | 20.26 | 20.31 | 20.34 | 20.44 | 20.57 | 22.81 | 23.3 | 23.38 | 23.32 | 21.04 | 20.58 | 20.36
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5B | 20.17 | 20.2 | 20.22 | 20.3 | 20.43 | 22.69 | 23.19 | 23.31 | 23.27 | 21.02 | 20.55 | 20.32
Outpatient | 90.1-2010 | ASHRAE 169-2006-5B | 20 | 20.09 | 20.14 | 20.27 | 20.45 | 21.46 | 21.81 | 21.85 | 21.74 | 20.71 | 20.35 | 20.11
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5B | 20.4 | 20.44 | 20.47 | 20.54 | 20.65 | 22.94 | 23.37 | 23.43 | 23.39 | 21.07 | 20.67 | 20.49
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5B | 19.33 | 19.49 | 19.59 | 19.83 | 20.16 | 22.58 | 23.24 | 23.31 | 23.11 | 20.64 | 19.97 | 19.51
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5B | 20.43 | 20.47 | 20.49 | 20.56 | 20.67 | 22.95 | 23.37 | 23.44 | 23.4 | 21.08 | 20.69 | 20.51
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5B | 19.89 | 19.99 | 20.06 | 20.2 | 20.41 | 20.6 | 20.83 | 20.85 | 20.72 | 20.51 | 20.24 | 19.99
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5B | 19.37 | 19.45 | 19.53 | 19.74 | 20.05 | 22.22 | 23 | 23.17 | 23.04 | 20.86 | 20.09 | 19.61
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5B | 20.27 | 20.33 | 20.36 | 20.45 | 20.59 | 22.89 | 23.35 | 23.42 | 23.35 | 21.01 | 20.59 | 20.37
Warehouse | 90.1-2010 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5B | 20.36 | 20.35 | 20.36 | 20.41 | 20.5 | 22.8 | 23.23 | 23.34 | 23.34 | 21.06 | 20.67 | 20.49
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
Hospital | 90.1-2013 | ASHRAE 169-2006-5B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5B | 20.57 | 20.59 | 20.61 | 20.66 | 20.73 | 22.99 | 23.39 | 23.46 | 23.43 | 21.14 | 20.79 | 20.64
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5B | 20.5 | 20.5 | 20.51 | 20.55 | 20.62 | 22.83 | 23.26 | 23.37 | 23.37 | 21.14 | 20.76 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
Outpatient | 90.1-2013 | ASHRAE 169-2006-5B | 20.33 | 20.34 | 20.36 | 20.42 | 20.51 | 21.47 | 21.73 | 21.81 | 21.79 | 20.86 | 20.6 | 20.44
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.96 | 23.33 | 23.42 | 23.44 | 21.17 | 20.86 | 20.74
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5B | 20.09 | 20.09 | 20.11 | 20.19 | 20.32 | 22.66 | 23.14 | 23.28 | 23.26 | 20.96 | 20.51 | 20.27
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5B | 20.67 | 20.66 | 20.66 | 20.68 | 20.72 | 22.97 | 23.34 | 23.43 | 23.44 | 21.18 | 20.87 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5B | 20.75 | 20.74 | 20.73 | 20.74 | 20.77 | 23.01 | 23.37 | 23.45 | 23.47 | 21.21 | 20.91 | 20.82
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5B | 20.25 | 20.27 | 20.3 | 20.37 | 20.47 | 20.6 | 20.74 | 20.8 | 20.76 | 20.67 | 20.51 | 20.36
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5B | 19.93 | 19.9 | 19.92 | 20.02 | 20.17 | 22.27 | 22.91 | 23.13 | 23.14 | 21.09 | 20.49 | 20.17
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5B | 20.58 | 20.57 | 20.58 | 20.6 | 20.66 | 22.92 | 23.31 | 23.4 | 23.41 | 21.14 | 20.81 | 20.68
Warehouse | 90.1-2013 | ASHRAE 169-2006-5B | 12.62 | 12.63 | 12.64 | 12.68 | 14.11 | 17.43 | 22.96 | 20.8 | 17.41 | 13.44 | 12.92 | 12.72
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 19.195 | 19.191 | 19.215 | 19.25 | 19.367 | 20.429 | 21.511 | 21.776 | 20.44 | 19.538 | 19.333 | 19.237
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-5B | 10.3 | 10.16 | 11.26 | 12.98 | 16.26 | 19.12 | 21.83 | 23.96 | 21.38 | 17.16 | 14.1 | 11.24
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-5C | 19.97 | 20 | 20.02 | 20.14 | 20.31 | 22.54 | 22.98 | 23.08 | 23.03 | 20.72 | 20.26 | 20.05
Hospital | 90.1-2004 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2004 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2004 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2004 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-5C | 19.97 | 20 | 20.02 | 20.14 | 20.31 | 22.54 | 22.98 | 23.08 | 23.03 | 20.72 | 20.26 | 20.05
Outpatient | 90.1-2004 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2004 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2004 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2004 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Hospital | 90.1-2007 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2007 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2007 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2007 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Outpatient | 90.1-2007 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2007 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2007 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2007 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5C | 19.98 | 20.01 | 20.03 | 20.16 | 20.32 | 22.62 | 23.03 | 23.11 | 23.06 | 20.7 | 20.26 | 20.06
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Hospital | 90.1-2010 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2010 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2010 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2010 | ASHRAE 169-2006-5C | 20.34 | 20.35 | 20.36 | 20.43 | 20.53 | 22.73 | 23.14 | 23.22 | 23.21 | 20.95 | 20.55 | 20.4
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-5C | 20.25 | 20.24 | 20.24 | 20.3 | 20.4 | 22.62 | 23.03 | 23.13 | 23.14 | 20.9 | 20.5 | 20.33
Outpatient | 90.1-2010 | ASHRAE 169-2006-5C | 20.11 | 20.14 | 20.16 | 20.26 | 20.4 | 21.36 | 21.59 | 21.65 | 21.59 | 20.59 | 20.32 | 20.16
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-5C | 20.47 | 20.47 | 20.48 | 20.54 | 20.62 | 22.87 | 23.23 | 23.31 | 23.3 | 20.99 | 20.65 | 20.52
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-5C | 19.52 | 19.58 | 19.62 | 19.81 | 20.06 | 22.39 | 22.85 | 22.94 | 22.84 | 20.43 | 19.9 | 19.63
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-5C | 20.49 | 20.5 | 20.5 | 20.56 | 20.63 | 22.88 | 23.24 | 23.32 | 23.31 | 21.01 | 20.67 | 20.55
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
SmallHotel | 90.1-2010 | ASHRAE 169-2006-5C | 20.01 | 20.05 | 20.08 | 20.19 | 20.35 | 20.49 | 20.6 | 20.63 | 20.56 | 20.38 | 20.2 | 20.06
SmallOffice | 90.1-2010 | ASHRAE 169-2006-5C | 19.55 | 19.56 | 19.59 | 19.75 | 19.98 | 22.06 | 22.66 | 22.82 | 22.78 | 20.65 | 20.02 | 19.69
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-5C | 20.35 | 20.36 | 20.37 | 20.45 | 20.55 | 22.81 | 23.18 | 23.26 | 23.24 | 20.92 | 20.56 | 20.41
Warehouse | 90.1-2010 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5C | 20.4 | 20.38 | 20.37 | 20.41 | 20.48 | 22.74 | 23.11 | 23.21 | 23.23 | 20.95 | 20.62 | 20.48
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
Hospital | 90.1-2013 | ASHRAE 169-2006-5C
LargeHotel | 90.1-2013 | ASHRAE 169-2006-5C | 20.62 | 20.61 | 20.61 | 20.65 | 20.71 | 22.95 | 23.29 | 23.37 | 23.37 | 21.08 | 20.77 | 20.66
LargeOffice | 90.1-2013 | ASHRAE 169-2006-5C
MediumOffice | 90.1-2013 | ASHRAE 169-2006-5C | 20.54 | 20.52 | 20.52 | 20.55 | 20.6 | 22.79 | 23.17 | 23.26 | 23.29 | 21.07 | 20.73 | 20.61
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
Outpatient | 90.1-2013 | ASHRAE 169-2006-5C | 20.38 | 20.37 | 20.37 | 20.42 | 20.49 | 21.42 | 21.62 | 21.68 | 21.69 | 20.76 | 20.55 | 20.44
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-5C | 20.68 | 20.66 | 20.65 | 20.66 | 20.7 | 22.93 | 23.27 | 23.35 | 23.38 | 21.12 | 20.83 | 20.73
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-5C | 20.15 | 20.13 | 20.13 | 20.19 | 20.29 | 22.58 | 22.98 | 23.09 | 23.1 | 20.81 | 20.43 | 20.26
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-5C | 20.69 | 20.67 | 20.66 | 20.68 | 20.71 | 22.94 | 23.28 | 23.36 | 23.39 | 21.13 | 20.84 | 20.75
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-5C | 20.76 | 20.74 | 20.73 | 20.74 | 20.77 | 22.99 | 23.33 | 23.4 | 23.43 | 21.17 | 20.89 | 20.81
SmallHotel | 90.1-2013 | ASHRAE 169-2006-5C | 20.3 | 20.3 | 20.31 | 20.37 | 20.45 | 20.54 | 20.61 | 20.66 | 20.64 | 20.56 | 20.46 | 20.35
SmallOffice | 90.1-2013 | ASHRAE 169-2006-5C | 20.01 | 19.97 | 19.96 | 20.04 | 20.16 | 22.19 | 22.75 | 22.92 | 22.96 | 20.93 | 20.41 | 20.16
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-5C | 20.61 | 20.59 | 20.58 | 20.6 | 20.65 | 22.89 | 23.23 | 23.32 | 23.34 | 21.08 | 20.77 | 20.67
Warehouse | 90.1-2013 | ASHRAE 169-2006-5C | 12.59 | 12.59 | 12.6 | 12.64 | 12.69 | 14.57 | 16.37 | 16.72 | 14.09 | 12.92 | 12.73 | 12.64
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.62 | 19.9 | 20.28 | 22.6 | 23.09 | 23.18 | 23.08 | 20.74 | 20.21 | 19.86
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.61 | 19.88 | 20.26 | 22.52 | 23.04 | 23.14 | 23.04 | 20.76 | 20.21 | 19.86
Hospital | 90.1-2004 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2004 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2004 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2004 | ASHRAE 169-2006-6A | 20.12 | 20.06 | 20.1 | 20.27 | 20.5 | 22.72 | 23.17 | 23.26 | 23.22 | 20.97 | 20.52 | 20.28
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-6A | 19.63 | 19.54 | 19.61 | 19.88 | 20.26 | 22.52 | 23.04 | 23.14 | 23.04 | 20.76 | 20.21 | 19.86
Outpatient | 90.1-2004 | ASHRAE 169-2006-6A | 19.82 | 19.76 | 19.82 | 20.04 | 20.36 | 21.34 | 21.64 | 21.7 | 21.61 | 20.62 | 20.28 | 20
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-6A | 20.29 | 20.24 | 20.27 | 20.4 | 20.59 | 22.86 | 23.26 | 23.34 | 23.31 | 21.01 | 20.63 | 20.42
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6A | 19.02 | 18.9 | 19.02 | 19.44 | 20 | 22.37 | 22.94 | 23.05 | 22.88 | 20.48 | 19.84 | 19.34
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-6A | 20.33 | 20.27 | 20.3 | 20.43 | 20.61 | 22.87 | 23.27 | 23.35 | 23.32 | 21.03 | 20.65 | 20.45
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-6A | 20.49 | 20.45 | 20.47 | 20.56 | 20.69 | 22.94 | 23.31 | 23.39 | 23.38 | 21.1 | 20.75 | 20.59
SmallHotel | 90.1-2004 | ASHRAE 169-2006-6A | 19.7 | 19.63 | 19.7 | 19.96 | 20.3 | 20.47 | 20.65 | 20.69 | 20.58 | 20.41 | 20.16 | 19.88
SmallOffice | 90.1-2004 | ASHRAE 169-2006-6A | 19.1 | 18.94 | 18.99 | 19.35 | 19.86 | 22.01 | 22.73 | 22.93 | 22.83 | 20.71 | 19.98 | 19.46
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-6A | 20.13 | 20.07 | 20.11 | 20.28 | 20.52 | 22.79 | 23.22 | 23.3 | 23.25 | 20.94 | 20.53 | 20.29
Warehouse | 90.1-2004 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6A | 20.16 | 20.06 | 20.06 | 20.18 | 20.37 | 22.67 | 23.1 | 23.21 | 23.21 | 20.93 | 20.55 | 20.33
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Hospital | 90.1-2007 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2007 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2007 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2007 | ASHRAE 169-2006-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Outpatient | 90.1-2007 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.1 | 20.22 | 20.41 | 21.36 | 21.62 | 21.7 | 21.68 | 20.75 | 20.5 | 20.31
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-6A | 20.55 | 20.49 | 20.49 | 20.54 | 20.64 | 22.9 | 23.26 | 23.35 | 23.37 | 21.11 | 20.79 | 20.65
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6A | 19.81 | 19.68 | 19.68 | 19.86 | 20.14 | 22.48 | 22.95 | 23.09 | 23.08 | 20.78 | 20.34 | 20.04
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-6A | 20.57 | 20.52 | 20.51 | 20.56 | 20.66 | 22.91 | 23.27 | 23.36 | 23.38 | 21.12 | 20.8 | 20.67
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
SmallHotel | 90.1-2007 | ASHRAE 169-2006-6A | 20.07 | 19.99 | 20 | 20.14 | 20.35 | 20.48 | 20.61 | 20.68 | 20.64 | 20.55 | 20.4 | 20.22
SmallOffice | 90.1-2007 | ASHRAE 169-2006-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-6A | 20.45 | 20.39 | 20.38 | 20.45 | 20.57 | 22.84 | 23.22 | 23.32 | 23.33 | 21.07 | 20.73 | 20.57
Warehouse | 90.1-2007 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6A | 20.16 | 20.06 | 20.06 | 20.18 | 20.37 | 22.67 | 23.1 | 23.21 | 23.21 | 20.93 | 20.55 | 20.33
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Hospital | 90.1-2010 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2010 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2010 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2010 | ASHRAE 169-2006-6A | 20.38 | 20.31 | 20.3 | 20.39 | 20.53 | 22.75 | 23.17 | 23.27 | 23.28 | 21.07 | 20.69 | 20.51
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-6A | 20.1 | 20.01 | 19.99 | 20.12 | 20.33 | 22.57 | 23.04 | 23.17 | 23.17 | 20.94 | 20.53 | 20.29
Outpatient | 90.1-2010 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.1 | 20.22 | 20.41 | 21.36 | 21.62 | 21.7 | 21.68 | 20.75 | 20.5 | 20.31
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-6A | 20.55 | 20.49 | 20.49 | 20.54 | 20.64 | 22.9 | 23.26 | 23.35 | 23.37 | 21.11 | 20.79 | 20.65
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6A | 19.81 | 19.68 | 19.68 | 19.86 | 20.14 | 22.48 | 22.95 | 23.09 | 23.08 | 20.78 | 20.34 | 20.04
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-6A | 20.57 | 20.52 | 20.51 | 20.56 | 20.66 | 22.91 | 23.27 | 23.36 | 23.38 | 21.12 | 20.8 | 20.67
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
SmallHotel | 90.1-2010 | ASHRAE 169-2006-6A | 20.07 | 19.99 | 20 | 20.14 | 20.35 | 20.48 | 20.61 | 20.68 | 20.64 | 20.55 | 20.4 | 20.22
SmallOffice | 90.1-2010 | ASHRAE 169-2006-6A | 19.67 | 19.51 | 19.48 | 19.66 | 19.96 | 22.08 | 22.73 | 22.95 | 22.96 | 20.93 | 20.34 | 19.97
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-6A | 20.45 | 20.39 | 20.38 | 20.45 | 20.57 | 22.84 | 23.22 | 23.32 | 23.33 | 21.07 | 20.73 | 20.57
Warehouse | 90.1-2010 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6A | 20.3 | 20.21 | 20.18 | 20.26 | 20.4 | 22.69 | 23.1 | 23.22 | 23.24 | 20.99 | 20.64 | 20.45
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
Hospital | 90.1-2013 | ASHRAE 169-2006-6A
LargeHotel | 90.1-2013 | ASHRAE 169-2006-6A | 20.67 | 20.63 | 20.62 | 20.66 | 20.72 | 22.97 | 23.32 | 23.4 | 23.42 | 21.16 | 20.87 | 20.75
LargeOffice | 90.1-2013 | ASHRAE 169-2006-6A
MediumOffice | 90.1-2013 | ASHRAE 169-2006-6A | 20.45 | 20.38 | 20.36 | 20.43 | 20.54 | 22.76 | 23.17 | 23.28 | 23.3 | 21.09 | 20.74 | 20.57
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
Outpatient | 90.1-2013 | ASHRAE 169-2006-6A | 20.26 | 20.19 | 20.17 | 20.27 | 20.42 | 21.37 | 21.61 | 21.7 | 21.7 | 20.79 | 20.56 | 20.4
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-6A | 20.63 | 20.57 | 20.55 | 20.59 | 20.66 | 22.91 | 23.27 | 23.36 | 23.39 | 21.14 | 20.84 | 20.72
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6A | 20.02 | 19.89 | 19.86 | 19.97 | 20.18 | 22.51 | 22.96 | 23.11 | 23.13 | 20.86 | 20.47 | 20.22
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-6A | 20.64 | 20.59 | 20.57 | 20.6 | 20.67 | 22.92 | 23.28 | 23.37 | 23.4 | 21.15 | 20.85 | 20.73
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-6A | 20.73 | 20.68 | 20.67 | 20.69 | 20.73 | 22.97 | 23.32 | 23.4 | 23.43 | 21.18 | 20.9 | 20.8
SmallHotel | 90.1-2013 | ASHRAE 169-2006-6A | 20.17 | 20.09 | 20.09 | 20.2 | 20.37 | 20.49 | 20.61 | 20.67 | 20.65 | 20.59 | 20.47 | 20.31
SmallOffice | 90.1-2013 | ASHRAE 169-2006-6A | 19.84 | 19.68 | 19.63 | 19.75 | 20 | 22.1 | 22.73 | 22.96 | 23 | 20.99 | 20.44 | 20.12
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-6A | 20.55 | 20.48 | 20.46 | 20.51 | 20.59 | 22.85 | 23.22 | 23.32 | 23.35 | 21.1 | 20.79 | 20.65
Warehouse | 90.1-2013 | ASHRAE 169-2006-6A | 12.51 | 12.46 | 12.47 | 12.56 | 14.45 | 16.87 | 19.89 | 19.39 | 15.2 | 13.13 | 12.81 | 12.63
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 19.332 | 19.336 | 19.402 | 19.499 | 20.187 | 21.576 | 22.125 | 22.272 | 20.641 | 19.872 | 19.644 | 19.476
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-6A | 10.22 | 10.09 | 11.25 | 13.04 | 16.38 | 19.29 | 22.13 | 24.19 | 21.66 | 17.31 | 14.18 | 11.25
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6B | 19.59 | 19.64 | 19.73 | 19.94 | 20.17 | 22.54 | 23.1 | 23.17 | 23.08 | 20.67 | 20.16 | 19.77
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-6B | 19.58 | 19.63 | 19.71 | 19.93 | 20.15 | 22.45 | 23.05 | 23.13 | 23.04 | 20.69 | 20.16 | 19.77
Hospital | 90.1-2004 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2004 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2004 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2004 | ASHRAE 169-2006-6B | 20.1 | 20.12 | 20.16 | 20.29 | 20.43 | 22.68 | 23.18 | 23.25 | 23.21 | 20.93 | 20.49 | 20.23
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-6B | 19.58 | 19.63 | 19.71 | 19.93 | 20.15 | 22.45 | 23.05 | 23.13 | 23.04 | 20.69 | 20.16 | 19.77
Outpatient | 90.1-2004 | ASHRAE 169-2006-6B | 19.79 | 19.83 | 19.9 | 20.08 | 20.27 | 21.29 | 21.64 | 21.69 | 21.6 | 20.56 | 20.23 | 19.93
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-6B | 20.27 | 20.29 | 20.32 | 20.43 | 20.54 | 22.83 | 23.26 | 23.33 | 23.3 | 20.98 | 20.6 | 20.38
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-6B | 18.96 | 19.04 | 19.18 | 19.51 | 19.84 | 22.28 | 22.96 | 23.04 | 22.88 | 20.39 | 19.76 | 19.21
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-6B | 20.31 | 20.32 | 20.35 | 20.45 | 20.56 | 22.84 | 23.27 | 23.34 | 23.32 | 21 | 20.62 | 20.41
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-6B | 20.48 | 20.48 | 20.5 | 20.58 | 20.65 | 22.92 | 23.32 | 23.39 | 23.38 | 21.07 | 20.73 | 20.56
SmallHotel | 90.1-2004 | ASHRAE 169-2006-6B | 19.66 | 19.71 | 19.79 | 20 | 20.2 | 20.41 | 20.66 | 20.68 | 20.57 | 20.35 | 20.11 | 19.8
SmallOffice | 90.1-2004 | ASHRAE 169-2006-6B | 19.02 | 19.05 | 19.11 | 19.42 | 19.74 | 21.91 | 22.73 | 22.9 | 22.82 | 20.61 | 19.89 | 19.33
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-6B | 20.11 | 20.13 | 20.18 | 20.31 | 20.45 | 22.75 | 23.22 | 23.29 | 23.25 | 20.9 | 20.49 | 20.23
Warehouse | 90.1-2004 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6B | 20.11 | 20.09 | 20.1 | 20.21 | 20.33 | 22.63 | 23.09 | 23.2 | 23.2 | 20.9 | 20.51 | 20.27
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Hospital | 90.1-2007 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2007 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2007 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2007 | ASHRAE 169-2006-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Outpatient | 90.1-2007 | ASHRAE 169-2006-6B | 20.12 | 20.13 | 20.14 | 20.25 | 20.36 | 21.32 | 21.62 | 21.69 | 21.67 | 20.72 | 20.47 | 20.26
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-6B | 20.53 | 20.51 | 20.51 | 20.56 | 20.62 | 22.87 | 23.26 | 23.35 | 23.37 | 21.09 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-6B | 19.74 | 19.73 | 19.74 | 19.9 | 20.07 | 22.42 | 22.95 | 23.08 | 23.07 | 20.73 | 20.28 | 19.95
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-6B | 20.55 | 20.53 | 20.53 | 20.58 | 20.63 | 22.89 | 23.27 | 23.36 | 23.38 | 21.1 | 20.79 | 20.64
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
SmallHotel | 90.1-2007 | ASHRAE 169-2006-6B | 20.02 | 20.03 | 20.05 | 20.18 | 20.3 | 20.43 | 20.61 | 20.67 | 20.63 | 20.51 | 20.36 | 20.15
SmallOffice | 90.1-2007 | ASHRAE 169-2006-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-6B | 20.42 | 20.41 | 20.41 | 20.47 | 20.55 | 22.81 | 23.22 | 23.31 | 23.33 | 21.04 | 20.71 | 20.53
Warehouse | 90.1-2007 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6B | 20.11 | 20.09 | 20.1 | 20.21 | 20.33 | 22.63 | 23.09 | 23.2 | 23.2 | 20.9 | 20.51 | 20.27
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Hospital | 90.1-2010 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2010 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2010 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2010 | ASHRAE 169-2006-6B | 20.34 | 20.33 | 20.33 | 20.42 | 20.5 | 22.71 | 23.17 | 23.27 | 23.28 | 21.04 | 20.66 | 20.47
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-6B | 20.05 | 20.04 | 20.04 | 20.16 | 20.28 | 22.53 | 23.03 | 23.16 | 23.16 | 20.91 | 20.48 | 20.22
Outpatient | 90.1-2010 | ASHRAE 169-2006-6B | 20.12 | 20.13 | 20.14 | 20.25 | 20.36 | 21.32 | 21.62 | 21.69 | 21.67 | 20.72 | 20.47 | 20.26
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-6B | 20.53 | 20.51 | 20.51 | 20.56 | 20.62 | 22.87 | 23.26 | 23.35 | 23.37 | 21.09 | 20.77 | 20.62
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-6B | 19.74 | 19.73 | 19.74 | 19.9 | 20.07 | 22.42 | 22.95 | 23.08 | 23.07 | 20.73 | 20.28 | 19.95
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-6B | 20.55 | 20.53 | 20.53 | 20.58 | 20.63 | 22.89 | 23.27 | 23.36 | 23.38 | 21.1 | 20.79 | 20.64
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
SmallHotel | 90.1-2010 | ASHRAE 169-2006-6B | 20.02 | 20.03 | 20.05 | 20.18 | 20.3 | 20.43 | 20.61 | 20.67 | 20.63 | 20.51 | 20.36 | 20.15
SmallOffice | 90.1-2010 | ASHRAE 169-2006-6B | 19.6 | 19.54 | 19.54 | 19.71 | 19.91 | 22.02 | 22.72 | 22.93 | 22.95 | 20.87 | 20.27 | 19.88
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-6B | 20.42 | 20.41 | 20.41 | 20.47 | 20.55 | 22.81 | 23.22 | 23.31 | 23.33 | 21.04 | 20.71 | 20.53
Warehouse | 90.1-2010 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6B | 20.26 | 20.22 | 20.21 | 20.29 | 20.37 | 22.66 | 23.09 | 23.21 | 23.24 | 20.96 | 20.61 | 20.4
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
Hospital | 90.1-2013 | ASHRAE 169-2006-6B
LargeHotel | 90.1-2013 | ASHRAE 169-2006-6B | 20.66 | 20.64 | 20.64 | 20.67 | 20.71 | 22.95 | 23.32 | 23.4 | 23.42 | 21.15 | 20.85 | 20.73
LargeOffice | 90.1-2013 | ASHRAE 169-2006-6B
MediumOffice | 90.1-2013 | ASHRAE 169-2006-6B | 20.42 | 20.4 | 20.38 | 20.45 | 20.52 | 22.73 | 23.17 | 23.27 | 23.29 | 21.07 | 20.71 | 20.53
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
Outpatient | 90.1-2013 | ASHRAE 169-2006-6B | 20.22 | 20.21 | 20.2 | 20.3 | 20.39 | 21.34 | 21.61 | 21.69 | 21.69 | 20.76 | 20.53 | 20.35
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-6B | 20.6 | 20.58 | 20.57 | 20.6 | 20.64 | 22.89 | 23.26 | 23.35 | 23.39 | 21.12 | 20.82 | 20.69
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-6B | 19.95 | 19.91 | 19.9 | 20.01 | 20.14 | 22.46 | 22.95 | 23.1 | 23.12 | 20.82 | 20.42 | 20.15
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-6B | 20.62 | 20.6 | 20.59 | 20.62 | 20.66 | 22.9 | 23.27 | 23.36 | 23.39 | 21.13 | 20.83 | 20.71
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-6B | 20.71 | 20.69 | 20.68 | 20.7 | 20.72 | 22.96 | 23.32 | 23.4 | 23.43 | 21.18 | 20.89 | 20.78
SmallHotel | 90.1-2013 | ASHRAE 169-2006-6B | 20.12 | 20.12 | 20.12 | 20.23 | 20.33 | 20.45 | 20.6 | 20.66 | 20.65 | 20.56 | 20.43 | 20.25
SmallOffice | 90.1-2013 | ASHRAE 169-2006-6B | 19.77 | 19.69 | 19.67 | 19.8 | 19.96 | 22.05 | 22.71 | 22.93 | 22.99 | 20.94 | 20.39 | 20.03
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-6B | 20.52 | 20.49 | 20.48 | 20.52 | 20.57 | 22.83 | 23.22 | 23.32 | 23.35 | 21.08 | 20.77 | 20.62
Warehouse | 90.1-2013 | ASHRAE 169-2006-6B | 12.48 | 12.48 | 12.5 | 12.57 | 12.65 | 15.81 | 19.34 | 18.33 | 14.81 | 13.04 | 12.75 | 12.57
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 19.119 | 19.149 | 19.147 | 19.203 | 19.279 | 20.043 | 21.32 | 20.987 | 19.824 | 19.408 | 19.293 | 19.174
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-6B | 10.24 | 10.13 | 11.21 | 12.96 | 16.3 | 19.16 | 21.87 | 23.95 | 21.47 | 17.19 | 14.1 | 11.21
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-7 | 19.32 | 19.24 | 19.44 | 19.7 | 19.96 | 22.42 | 22.92 | 22.99 | 22.88 | 20.51 | 19.98 | 19.55
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-7 | 19.81 | 19.7 | 19.79 | 19.93 | 20.09 | 22.41 | 22.9 | 23.01 | 23 | 20.75 | 20.31 | 20
Hospital | 90.1-2004 | ASHRAE 169-2006-7
LargeHotel | 90.1-2004 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2004 | ASHRAE 169-2006-7
MediumOffice | 90.1-2004 | ASHRAE 169-2006-7A | 19.93 | 19.87 | 19.98 | 20.14 | 20.29 | 22.6 | 23.06 | 23.14 | 23.09 | 20.82 | 20.37 | 20.09
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-7 | 19.81 | 19.7 | 19.79 | 19.93 | 20.09 | 22.41 | 22.9 | 23.01 | 23 | 20.75 | 20.31 | 20
Outpatient | 90.1-2004 | ASHRAE 169-2006-7 | 19.57 | 19.5 | 19.66 | 19.88 | 20.09 | 21.19 | 21.5 | 21.54 | 21.44 | 20.43 | 20.08 | 19.75
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-7 | 20.13 | 20.08 | 20.17 | 20.3 | 20.43 | 22.76 | 23.17 | 23.24 | 23.2 | 20.9 | 20.5 | 20.27
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-7 | 18.57 | 18.47 | 18.76 | 19.16 | 19.54 | 22.11 | 22.71 | 22.78 | 22.59 | 20.16 | 19.49 | 18.9
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-7 | 20.18 | 20.13 | 20.21 | 20.34 | 20.45 | 22.78 | 23.19 | 23.25 | 23.22 | 20.92 | 20.53 | 20.3
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-7 | 20.38 | 20.34 | 20.4 | 20.49 | 20.57 | 22.87 | 23.25 | 23.32 | 23.3 | 21.01 | 20.67 | 20.48
SmallHotel | 90.1-2004 | ASHRAE 169-2006-7 | 19.41 | 19.35 | 19.54 | 19.78 | 20.01 | 20.3 | 20.5 | 20.52 | 20.39 | 20.2 | 19.94 | 19.6
SmallOffice | 90.1-2004 | ASHRAE 169-2006-7 | 18.67 | 18.5 | 18.73 | 19.07 | 19.43 | 21.75 | 22.5 | 22.67 | 22.56 | 20.4 | 19.65 | 19.05
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-7 | 19.94 | 19.88 | 20 | 20.16 | 20.31 | 22.68 | 23.11 | 23.18 | 23.12 | 20.8 | 20.38 | 20.1
Warehouse | 90.1-2004 | ASHRAE 169-2006-7A | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-7 | 20.06 | 19.96 | 20 | 20.1 | 20.21 | 22.55 | 22.98 | 23.09 | 23.11 | 20.83 | 20.46 | 20.22
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Hospital | 90.1-2007 | ASHRAE 169-2006-7
LargeHotel | 90.1-2007 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2007 | ASHRAE 169-2006-7
MediumOffice | 90.1-2007 | ASHRAE 169-2006-7A | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Outpatient | 90.1-2007 | ASHRAE 169-2006-7 | 20.05 | 19.97 | 20.02 | 20.13 | 20.24 | 21.24 | 21.51 | 21.58 | 21.57 | 20.64 | 20.41 | 20.19
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-7 | 20.5 | 20.44 | 20.45 | 20.5 | 20.56 | 22.83 | 23.2 | 23.29 | 23.31 | 21.06 | 20.75 | 20.6
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-7 | 19.68 | 19.54 | 19.6 | 19.74 | 19.91 | 22.31 | 22.79 | 22.93 | 22.93 | 20.64 | 20.22 | 19.9
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-7 | 20.53 | 20.47 | 20.48 | 20.52 | 20.58 | 22.85 | 23.22 | 23.3 | 23.33 | 21.07 | 20.76 | 20.62
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
SmallHotel | 90.1-2007 | ASHRAE 169-2006-7 | 19.94 | 19.85 | 19.92 | 20.04 | 20.17 | 20.35 | 20.49 | 20.55 | 20.52 | 20.43 | 20.3 | 20.08
SmallOffice | 90.1-2007 | ASHRAE 169-2006-7 | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-7 | 20.39 | 20.32 | 20.34 | 20.4 | 20.47 | 22.76 | 23.15 | 23.24 | 23.26 | 21 | 20.68 | 20.51
Warehouse | 90.1-2007 | ASHRAE 169-2006-7A | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-7 | 20.06 | 19.96 | 20 | 20.1 | 20.21 | 22.55 | 22.98 | 23.09 | 23.11 | 20.83 | 20.46 | 20.22
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Hospital | 90.1-2010 | ASHRAE 169-2006-7
LargeHotel | 90.1-2010 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2010 | ASHRAE 169-2006-7
MediumOffice | 90.1-2010 | ASHRAE 169-2006-7A | 20.28 | 20.21 | 20.24 | 20.32 | 20.41 | 22.65 | 23.09 | 23.19 | 23.2 | 20.98 | 20.62 | 20.41
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-7 | 19.89 | 19.78 | 19.85 | 19.98 | 20.12 | 22.42 | 22.91 | 23.02 | 23.02 | 20.79 | 20.37 | 20.08
Outpatient | 90.1-2010 | ASHRAE 169-2006-7 | 20.05 | 19.97 | 20.02 | 20.13 | 20.24 | 21.24 | 21.51 | 21.58 | 21.57 | 20.64 | 20.41 | 20.19
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-7 | 20.5 | 20.44 | 20.45 | 20.5 | 20.56 | 22.83 | 23.2 | 23.29 | 23.31 | 21.06 | 20.75 | 20.6
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-7 | 19.68 | 19.54 | 19.6 | 19.74 | 19.91 | 22.31 | 22.79 | 22.93 | 22.93 | 20.64 | 20.22 | 19.9
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-7 | 20.53 | 20.47 | 20.48 | 20.52 | 20.58 | 22.85 | 23.22 | 23.3 | 23.33 | 21.07 | 20.76 | 20.62
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
SmallHotel | 90.1-2010 | ASHRAE 169-2006-7 | 19.94 | 19.85 | 19.92 | 20.04 | 20.17 | 20.35 | 20.49 | 20.55 | 20.52 | 20.43 | 20.3 | 20.08
SmallOffice | 90.1-2010 | ASHRAE 169-2006-7 | 19.49 | 19.31 | 19.35 | 19.52 | 19.72 | 21.89 | 22.56 | 22.77 | 22.8 | 20.76 | 20.19 | 19.78
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-7 | 20.39 | 20.32 | 20.34 | 20.4 | 20.47 | 22.76 | 23.15 | 23.24 | 23.26 | 21 | 20.68 | 20.51
Warehouse | 90.1-2010 | ASHRAE 169-2006-7A | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-7 | 20.13 | 20.03 | 20.05 | 20.13 | 20.23 | 22.56 | 22.99 | 23.1 | 23.13 | 20.86 | 20.51 | 20.29
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
Hospital | 90.1-2013 | ASHRAE 169-2006-7
LargeHotel | 90.1-2013 | ASHRAE 169-2006-7 | 20.64 | 20.59 | 20.6 | 20.63 | 20.66 | 22.92 | 23.27 | 23.36 | 23.38 | 21.13 | 20.84 | 20.72
LargeOffice | 90.1-2013 | ASHRAE 169-2006-7
MediumOffice | 90.1-2013 | ASHRAE 169-2006-7A | 20.32 | 20.24 | 20.27 | 20.34 | 20.42 | 22.66 | 23.09 | 23.19 | 23.21 | 21 | 20.64 | 20.44
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
Outpatient | 90.1-2013 | ASHRAE 169-2006-7 | 20.1 | 20.01 | 20.06 | 20.15 | 20.26 | 21.25 | 21.51 | 21.59 | 21.58 | 20.66 | 20.44 | 20.23
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-7 | 20.54 | 20.48 | 20.48 | 20.52 | 20.57 | 22.84 | 23.21 | 23.3 | 23.33 | 21.07 | 20.77 | 20.63
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-7 | 19.77 | 19.63 | 19.67 | 19.79 | 19.94 | 22.33 | 22.8 | 22.94 | 22.96 | 20.68 | 20.28 | 19.99
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-7 | 20.56 | 20.5 | 20.51 | 20.54 | 20.59 | 22.85 | 23.22 | 23.31 | 23.34 | 21.08 | 20.78 | 20.65
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-7 | 20.66 | 20.62 | 20.62 | 20.64 | 20.67 | 22.92 | 23.28 | 23.36 | 23.39 | 21.14 | 20.85 | 20.74
SmallHotel | 90.1-2013 | ASHRAE 169-2006-7 | 19.99 | 19.9 | 19.96 | 20.07 | 20.19 | 20.35 | 20.49 | 20.55 | 20.53 | 20.45 | 20.33 | 20.12
SmallOffice | 90.1-2013 | ASHRAE 169-2006-7 | 19.57 | 19.38 | 19.42 | 19.56 | 19.75 | 21.9 | 22.56 | 22.78 | 22.82 | 20.8 | 20.24 | 19.85
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-7 | 20.44 | 20.37 | 20.38 | 20.42 | 20.49 | 22.77 | 23.15 | 23.25 | 23.28 | 21.02 | 20.7 | 20.55
Warehouse | 90.1-2013 | ASHRAE 169-2006-7A | 12.35 | 12.31 | 12.37 | 12.47 | 12.56 | 14.73 | 17.7 | 16.37 | 13.17 | 12.78 | 12.62 | 12.44
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-7A | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7A | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-7 | 19.18 | 19.14 | 19.229 | 19.325 | 19.396 | 19.767 | 20.94 | 20.468 | 19.761 | 19.556 | 19.433 | 19.279
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-7A | 10.19 | 10.01 | 11.18 | 12.98 | 16.32 | 19.27 | 22.11 | 24.18 | 21.63 | 17.28 | 14.14 | 11.19
FullServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-8 | 19.43 | 19.32 | 19.4 | 19.59 | 19.87 | 22.29 | 22.74 | 22.87 | 22.84 | 20.5 | 19.92 | 19.66
HighriseApartment | 90.1-2004 | ASHRAE 169-2006-8 | 19.33 | 19.22 | 19.3 | 19.5 | 19.79 | 22.17 | 22.67 | 22.81 | 22.78 | 20.49 | 19.87 | 19.58
Hospital | 90.1-2004 | ASHRAE 169-2006-8
LargeHotel | 90.1-2004 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2004 | ASHRAE 169-2006-8
MediumOffice | 90.1-2004 | ASHRAE 169-2006-8A | 19.87 | 19.79 | 19.85 | 19.98 | 20.18 | 22.48 | 22.93 | 23.03 | 23.02 | 20.76 | 20.24 | 20.04
MidriseApartment | 90.1-2004 | ASHRAE 169-2006-8 | 19.33 | 19.22 | 19.3 | 19.5 | 19.79 | 22.17 | 22.67 | 22.81 | 22.78 | 20.49 | 19.87 | 19.58
Outpatient | 90.1-2004 | ASHRAE 169-2006-8 | 19.51 | 19.42 | 19.51 | 19.69 | 19.95 | 21.02 | 21.31 | 21.39 | 21.34 | 20.35 | 19.92 | 19.7
PrimarySchool | 90.1-2004 | ASHRAE 169-2006-8 | 20.17 | 20.11 | 20.14 | 20.24 | 20.37 | 22.69 | 23.08 | 23.17 | 23.17 | 20.88 | 20.46 | 20.3
QuickServiceRestaurant | 90.1-2004 | ASHRAE 169-2006-8 | 18.77 | 18.62 | 18.75 | 19.02 | 19.42 | 21.94 | 22.46 | 22.61 | 22.56 | 20.16 | 19.45 | 19.08
RetailStandalone | 90.1-2004 | ASHRAE 169-2006-8 | 20.22 | 20.15 | 20.19 | 20.27 | 20.4 | 22.71 | 23.1 | 23.19 | 23.19 | 20.9 | 20.49 | 20.34
SecondarySchool | 90.1-2004 | ASHRAE 169-2006-8 | 20.41 | 20.36 | 20.38 | 20.44 | 20.53 | 22.82 | 23.18 | 23.27 | 23.28 | 21 | 20.64 | 20.51
SmallHotel | 90.1-2004 | ASHRAE 169-2006-8 | 19.34 | 19.25 | 19.35 | 19.56 | 19.86 | 20.11 | 20.27 | 20.34 | 20.27 | 20.1 | 19.76 | 19.54
SmallOffice | 90.1-2004 | ASHRAE 169-2006-8 | 18.59 | 18.4 | 18.47 | 18.75 | 19.2 | 21.51 | 22.24 | 22.47 | 22.45 | 20.31 | 19.46 | 18.99
RetailStripmall | 90.1-2004 | ASHRAE 169-2006-8 | 19.99 | 19.92 | 19.97 | 20.08 | 20.25 | 22.59 | 23 | 23.09 | 23.09 | 20.79 | 20.33 | 20.15
Warehouse | 90.1-2004 | ASHRAE 169-2006-8A | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-8 | 19.57 | 19.46 | 19.52 | 19.67 | 19.9 | 22.31 | 22.76 | 22.89 | 22.89 | 20.57 | 20.04 | 19.79
HighriseApartment | 90.1-2007 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Hospital | 90.1-2007 | ASHRAE 169-2006-8
LargeHotel | 90.1-2007 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2007 | ASHRAE 169-2006-8
MediumOffice | 90.1-2007 | ASHRAE 169-2006-8A | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MidriseApartment | 90.1-2007 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Outpatient | 90.1-2007 | ASHRAE 169-2006-8 | 19.59 | 19.51 | 19.57 | 19.73 | 19.98 | 21.03 | 21.31 | 21.4 | 21.37 | 20.39 | 20 | 19.78
PrimarySchool | 90.1-2007 | ASHRAE 169-2006-8 | 20.25 | 20.18 | 20.2 | 20.28 | 20.39 | 22.7 | 23.09 | 23.18 | 23.2 | 20.92 | 20.52 | 20.37
QuickServiceRestaurant | 90.1-2007 | ASHRAE 169-2006-8 | 18.97 | 18.82 | 18.91 | 19.13 | 19.48 | 21.97 | 22.49 | 22.65 | 22.63 | 20.27 | 19.61 | 19.27
RetailStandalone | 90.1-2007 | ASHRAE 169-2006-8 | 20.28 | 20.22 | 20.24 | 20.31 | 20.42 | 22.72 | 23.1 | 23.2 | 23.22 | 20.94 | 20.55 | 20.4
SecondarySchool | 90.1-2007 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
SmallHotel | 90.1-2007 | ASHRAE 169-2006-8 | 19.43 | 19.34 | 19.42 | 19.61 | 19.88 | 20.11 | 20.28 | 20.35 | 20.3 | 20.15 | 19.84 | 19.63
SmallOffice | 90.1-2007 | ASHRAE 169-2006-8 | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
RetailStripmall | 90.1-2007 | ASHRAE 169-2006-8 | 20.08 | 20.01 | 20.04 | 20.13 | 20.27 | 22.6 | 23.01 | 23.11 | 23.12 | 20.83 | 20.4 | 20.23
Warehouse | 90.1-2007 | ASHRAE 169-2006-8A | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-8 | 19.57 | 19.46 | 19.52 | 19.67 | 19.9 | 22.31 | 22.76 | 22.89 | 22.89 | 20.57 | 20.04 | 19.79
HighriseApartment | 90.1-2010 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Hospital | 90.1-2010 | ASHRAE 169-2006-8
LargeHotel | 90.1-2010 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2010 | ASHRAE 169-2006-8
MediumOffice | 90.1-2010 | ASHRAE 169-2006-8A | 19.93 | 19.85 | 19.9 | 20.02 | 20.2 | 22.49 | 22.93 | 23.05 | 23.04 | 20.79 | 20.3 | 20.1
MidriseApartment | 90.1-2010 | ASHRAE 169-2006-8 | 19.39 | 19.28 | 19.35 | 19.53 | 19.81 | 22.18 | 22.68 | 22.82 | 22.81 | 20.53 | 19.92 | 19.64
Outpatient | 90.1-2010 | ASHRAE 169-2006-8 | 19.59 | 19.51 | 19.57 | 19.73 | 19.98 | 21.03 | 21.31 | 21.4 | 21.37 | 20.39 | 20 | 19.78
PrimarySchool | 90.1-2010 | ASHRAE 169-2006-8 | 20.25 | 20.18 | 20.2 | 20.28 | 20.39 | 22.7 | 23.09 | 23.18 | 23.2 | 20.92 | 20.52 | 20.37
QuickServiceRestaurant | 90.1-2010 | ASHRAE 169-2006-8 | 18.97 | 18.82 | 18.91 | 19.13 | 19.48 | 21.97 | 22.49 | 22.65 | 22.63 | 20.27 | 19.61 | 19.27
RetailStandalone | 90.1-2010 | ASHRAE 169-2006-8 | 20.28 | 20.22 | 20.24 | 20.31 | 20.42 | 22.72 | 23.1 | 23.2 | 23.22 | 20.94 | 20.55 | 20.4
SecondarySchool | 90.1-2010 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
SmallHotel | 90.1-2010 | ASHRAE 169-2006-8 | 19.43 | 19.34 | 19.42 | 19.61 | 19.88 | 20.11 | 20.28 | 20.35 | 20.3 | 20.15 | 19.84 | 19.63
SmallOffice | 90.1-2010 | ASHRAE 169-2006-8 | 18.74 | 18.54 | 18.59 | 18.83 | 19.25 | 21.53 | 22.25 | 22.5 | 22.5 | 20.4 | 19.58 | 19.13
RetailStripmall | 90.1-2010 | ASHRAE 169-2006-8 | 20.08 | 20.01 | 20.04 | 20.13 | 20.27 | 22.6 | 23.01 | 23.11 | 23.12 | 20.83 | 20.4 | 20.23
Warehouse | 90.1-2010 | ASHRAE 169-2006-8A | 12.06 | 12.03 | 12.11 | 12.25 | 12.43 | 14.32 | 16.06 | 13.56 | 12.74 | 12.53 | 12.29 | 12.17
FullServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-8 | 19.66 | 19.55 | 19.59 | 19.71 | 19.93 | 22.32 | 22.77 | 22.91 | 22.92 | 20.62 | 20.11 | 19.87
HighriseApartment | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91
Hospital | 90.1-2013 | ASHRAE 169-2006-8
LargeHotel | 90.1-2013 | ASHRAE 169-2006-8 | 20.46 | 20.41 | 20.42 | 20.47 | 20.55 | 22.83 | 23.19 | 23.28 | 23.3 | 21.03 | 20.68 | 20.56
LargeOffice | 90.1-2013 | ASHRAE 169-2006-8
MediumOffice | 90.1-2013 | ASHRAE 169-2006-8A | 20.12 | 20.04 | 20.06 | 20.13 | 20.27 | 22.53 | 22.96 | 23.08 | 23.1 | 20.88 | 20.44 | 20.27
MidriseApartment | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91
Outpatient | 90.1-2013 | ASHRAE 169-2006-8 | 19.83 | 19.74 | 19.77 | 19.88 | 20.06 | 21.08 | 21.34 | 21.43 | 21.43 | 20.49 | 20.17 | 19.99
PrimarySchool | 90.1-2013 | ASHRAE 169-2006-8 | 20.29 | 20.23 | 20.24 | 20.3 | 20.41 | 22.71 | 23.09 | 23.19 | 23.21 | 20.94 | 20.56 | 20.41
QuickServiceRestaurant | 90.1-2013 | ASHRAE 169-2006-8 | 19.1 | 18.95 | 19.01 | 19.2 | 19.51 | 21.99 | 22.5 | 22.67 | 22.67 | 20.34 | 19.72 | 19.39
RetailStandalone | 90.1-2013 | ASHRAE 169-2006-8 | 20.33 | 20.26 | 20.28 | 20.33 | 20.43 | 22.73 | 23.11 | 23.21 | 23.23 | 20.96 | 20.59 | 20.44
SecondarySchool | 90.1-2013 | ASHRAE 169-2006-8 | 20.49 | 20.44 | 20.44 | 20.48 | 20.56 | 22.83 | 23.19 | 23.28 | 23.31 | 21.05 | 20.71 | 20.59
SmallHotel | 90.1-2013 | ASHRAE 169-2006-8 | 19.7 | 19.61 | 19.65 | 19.78 | 19.98 | 20.16 | 20.3 | 20.38 | 20.36 | 20.27 | 20.05 | 19.87
SmallOffice | 90.1-2013 | ASHRAE 169-2006-8 | 18.84 | 18.64 | 18.67 | 18.89 | 19.27 | 21.55 | 22.26 | 22.51 | 22.54 | 20.45 | 19.66 | 19.22
RetailStripmall | 90.1-2013 | ASHRAE 169-2006-8 | 20.14 | 20.06 | 20.08 | 20.16 | 20.29 | 22.61 | 23.01 | 23.12 | 23.14 | 20.86 | 20.45 | 20.28
Warehouse | 90.1-2013 | ASHRAE 169-2006-8A | 12.29 | 12.25 | 12.28 | 12.35 | 12.46 | 14.3 | 16.04 | 13.55 | 12.77 | 12.63 | 12.48 | 12.38
FullServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref 1980-2004 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref 1980-2004 | ASHRAE 169-2006-8A | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
FullServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Hospital | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
LargeOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MediumOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-8A | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
MidriseApartment | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Outpatient | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
PrimarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
QuickServiceRestaurant | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStandalone | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SecondarySchool | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallHotel | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
SmallOffice | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
RetailStripmall | DOE Ref Pre-1980 | ASHRAE 169-2006-8 | 18.433 | 18.408 | 18.536 | 18.706 | 18.864 | 19.112 | 19.608 | 19.23 | 19.106 | 18.966 | 18.725 | 18.567
Warehouse | DOE Ref Pre-1980 | ASHRAE 169-2006-8A | 9.87 | 9.72 | 10.93 | 12.79 | 16.23 | 19.19 | 22.03 | 24.08 | 21.53 | 17.14 | 13.85 | 10.9
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-0A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-0B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-3A | 20.51 | 20.47 | 20.58 | 20.67 | 20.76 | 22.99 | 23.41 | 23.51 | 23.52 | 21.26 | 20.86 | 20.68
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-3B | 20.62 | 20.6 | 20.62 | 20.72 | 20.85 | 23.12 | 23.5 | 23.59 | 23.6 | 21.35 | 20.94 | 20.73
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-3C | 20.67 | 20.66 | 20.63 | 20.67 | 20.7 | 22.85 | 23.24 | 23.33 | 23.34 | 21.19 | 20.85 | 20.74
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-4A | 20.39 | 20.3 | 20.32 | 20.39 | 20.5 | 22.77 | 23.22 | 23.35 | 23.37 | 21.13 | 20.73 | 20.53
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-4B | 20.46 | 20.41 | 20.44 | 20.52 | 20.63 | 22.88 | 23.33 | 23.45 | 23.45 | 21.21 | 20.78 | 20.57
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-4C | 20.38 | 20.34 | 20.37 | 20.42 | 20.49 | 22.68 | 23.08 | 23.2 | 23.22 | 21 | 20.63 | 20.48
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-5A | 20.27 | 20.17 | 20.19 | 20.27 | 20.38 | 22.64 | 23.1 | 23.22 | 23.23 | 21 | 20.62 | 20.42
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-5B | 20.31 | 20.26 | 20.3 | 20.32 | 20.42 | 22.72 | 23.17 | 23.28 | 23.32 | 21.04 | 20.61 | 20.42
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-5C | 20.3 | 20.28 | 20.27 | 20.32 | 20.39 | 22.59 | 22.98 | 23.09 | 23.12 | 20.91 | 20.54 | 20.4
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-6A | 20.23 | 20.13 | 20.17 | 20.26 | 20.37 | 22.62 | 23.07 | 23.19 | 23.23 | 20.99 | 20.6 | 20.38
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-6B | 20.28 | 20.22 | 20.24 | 20.3 | 20.35 | 22.6 | 23.05 | 23.18 | 23.21 | 20.98 | 20.63 | 20.46
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-7A | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-7B | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-8A | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2013-8B | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
MidriseApartment | NREL ZNE Ready 2017 | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-0A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-0B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-1A | 21.12 | 21.09 | 21.1 | 21.12 | 21.16 | 23.3 | 23.66 | 23.73 | 23.76 | 21.58 | 21.28 | 21.19
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-1B | 20.81 | 20.84 | 20.99 | 21.2 | 21.38 | 23.56 | 23.83 | 23.83 | 23.83 | 21.62 | 21.21 | 20.96
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-2A | 20.72 | 20.73 | 20.77 | 20.9 | 21.08 | 23.26 | 23.62 | 23.68 | 23.69 | 21.49 | 21.08 | 20.89
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-2B | 20.72 | 20.65 | 20.7 | 20.92 | 21.08 | 23.36 | 23.73 | 23.8 | 23.79 | 21.46 | 20.98 | 20.72
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-3A | 20.51 | 20.47 | 20.58 | 20.67 | 20.76 | 22.99 | 23.41 | 23.51 | 23.52 | 21.26 | 20.86 | 20.68
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-3B | 20.62 | 20.6 | 20.62 | 20.72 | 20.85 | 23.12 | 23.5 | 23.59 | 23.6 | 21.35 | 20.94 | 20.73
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-3C | 20.67 | 20.66 | 20.63 | 20.67 | 20.7 | 22.85 | 23.24 | 23.33 | 23.34 | 21.19 | 20.85 | 20.74
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-4A | 20.39 | 20.3 | 20.32 | 20.39 | 20.5 | 22.77 | 23.22 | 23.35 | 23.37 | 21.13 | 20.73 | 20.53
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-4B | 20.46 | 20.41 | 20.44 | 20.52 | 20.63 | 22.88 | 23.33 | 23.45 | 23.45 | 21.21 | 20.78 | 20.57
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-4C | 20.38 | 20.34 | 20.37 | 20.42 | 20.49 | 22.68 | 23.08 | 23.2 | 23.22 | 21 | 20.63 | 20.48
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-5A | 20.27 | 20.17 | 20.19 | 20.27 | 20.38 | 22.64 | 23.1 | 23.22 | 23.23 | 21 | 20.62 | 20.42
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-5B | 20.31 | 20.26 | 20.3 | 20.32 | 20.42 | 22.72 | 23.17 | 23.28 | 23.32 | 21.04 | 20.61 | 20.42
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-5C | 20.3 | 20.28 | 20.27 | 20.32 | 20.39 | 22.59 | 22.98 | 23.09 | 23.12 | 20.91 | 20.54 | 20.4
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-6A | 20.23 | 20.13 | 20.17 | 20.26 | 20.37 | 22.62 | 23.07 | 23.19 | 23.23 | 20.99 | 20.6 | 20.38
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-6B | 20.28 | 20.22 | 20.24 | 20.3 | 20.35 | 22.6 | 23.05 | 23.18 | 23.21 | 20.98 | 20.63 | 20.46
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-7A | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-7B | 20.06 | 20 | 20 | 20.1 | 20.25 | 22.52 | 22.97 | 23.09 | 23.12 | 20.89 | 20.5 | 20.25
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-8A | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2013-8B | 19.79 | 19.74 | 19.74 | 19.85 | 20.04 | 22.34 | 22.8 | 22.93 | 22.95 | 20.71 | 20.2 | 19.92
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-1A | 21 | 20.99 | 21.02 | 21.1 | 21.15 | 23.31 | 23.66 | 23.73 | 23.74 | 21.53 | 21.21 | 21.08
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-1B | 20.86 | 20.88 | 20.96 | 21.12 | 21.31 | 23.58 | 23.95 | 24.07 | 24.06 | 21.76 | 21.31 | 21.02
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-2A | 20.58 | 20.52 | 20.65 | 20.79 | 20.95 | 23.17 | 23.56 | 23.64 | 23.64 | 21.38 | 20.98 | 20.69
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-2B | 20.67 | 20.65 | 20.8 | 20.96 | 21.1 | 23.42 | 23.86 | 23.93 | 23.91 | 21.56 | 21.11 | 20.79
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-3A | 20.51 | 20.47 | 20.53 | 20.63 | 20.76 | 23.01 | 23.42 | 23.52 | 23.54 | 21.26 | 20.88 | 20.67
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-3B | 20.61 | 20.57 | 20.64 | 20.69 | 20.81 | 23.09 | 23.51 | 23.58 | 23.59 | 21.34 | 20.93 | 20.74
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-3C | 20.51 | 20.51 | 20.5 | 20.53 | 20.57 | 22.72 | 23.1 | 23.17 | 23.21 | 21.06 | 20.73 | 20.59
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-4A | 20.36 | 20.28 | 20.33 | 20.4 | 20.52 | 22.79 | 23.23 | 23.36 | 23.37 | 21.14 | 20.74 | 20.51
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-4B | 20.43 | 20.4 | 20.43 | 20.49 | 20.63 | 22.88 | 23.32 | 23.43 | 23.44 | 21.2 | 20.77 | 20.57
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-4C | 20.37 | 20.35 | 20.36 | 20.38 | 20.46 | 22.68 | 23.09 | 23.21 | 23.24 | 21.02 | 20.63 | 20.48
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-5A | 20.25 | 20.17 | 20.19 | 20.28 | 20.41 | 22.7 | 23.15 | 23.26 | 23.29 | 21.04 | 20.65 | 20.43
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-5B | 20.27 | 20.27 | 20.29 | 20.35 | 20.45 | 22.7 | 23.17 | 23.31 | 23.29 | 21.06 | 20.62 | 20.42
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-5C | 20.32 | 20.31 | 20.3 | 20.35 | 20.43 | 22.64 | 23.05 | 23.15 | 23.17 | 20.94 | 20.57 | 20.41
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-6A | 20.28 | 20.19 | 20.16 | 20.24 | 20.38 | 22.61 | 23.05 | 23.18 | 23.2 | 21 | 20.63 | 20.43
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-6B | 20.24 | 20.2 | 20.19 | 20.26 | 20.35 | 22.58 | 23.05 | 23.17 | 23.2 | 20.98 | 20.59 | 20.38
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-7 | 20.1 | 20 | 20.03 | 20.11 | 20.21 | 22.48 | 22.94 | 23.06 | 23.08 | 20.88 | 20.49 | 20.26
MidriseApartment | ZE AEDG Multifamily | ASHRAE 169-2006-8 | 19.7 | 19.58 | 19.61 | 19.72 | 19.92 | 22.24 | 22.72 | 22.87 | 22.89 | 20.66 | 20.14 | 19.91

## HVAC Inference
HVAC inference
Template | Size Category | Heating Source | Cooling Source | Delivery Type | HVAC System Type | Central Heating Fuel | Zone Heating Fuel | Cooling Fuel
Any | res_small | NaturalGas | Electricity | air | PTAC | NaturalGas |  | Electricity
Any | res_med | NaturalGas | Electricity | air | PTAC | NaturalGas |  | Electricity
Any | nonres_small | NaturalGas | Electricity | air | PSZ-AC | NaturalGas |  | Electricity
Any | nonres_med | NaturalGas | Electricity | air | PVAV Reheat | NaturalGas | NaturalGas | Electricity
Any | nonres_lg | NaturalGas | Electricity | air | VAV Reheat | NaturalGas | NaturalGas | Electricity
Any | res_small | Electricity | Electricity | air | PTHP | Electricity |  | Electricity
Any | res_med | Electricity | Electricity | air | PTHP | Electricity |  | Electricity
Any | nonres_small | Electricity | Electricity | air | PSZ-HP | Electricity |  | Electricity
Any | nonres_med | Electricity | Electricity | air | PVAV PFP Boxes | Electricity | Electricity | Electricity
Any | nonres_lg | Electricity | Electricity | air | VAV PFP Boxes | Electricity | Electricity | Electricity
Any | res_small | DistrictHeating | Electricity | air | PTAC | DistrictHeating |  | Electricity
Any | res_med | DistrictHeating | Electricity | air | PTAC | DistrictHeating |  | Electricity
Any | nonres_small | DistrictHeating | Electricity | air | PVAV Reheat | DistrictHeating | DistrictHeating | Electricity
Any | nonres_med | DistrictHeating | Electricity | air | PVAV Reheat | DistrictHeating | DistrictHeating | Electricity
Any | nonres_lg | DistrictHeating | Electricity | air | VAV Reheat | DistrictHeating | DistrictHeating | Electricity
Any | res_small | AirSourceHeatPump | Electricity | air | PTAC | AirSourceHeatPump |  | Electricity
Any | res_med | AirSourceHeatPump | Electricity | air | PTAC | AirSourceHeatPump |  | Electricity
Any | nonres_small | AirSourceHeatPump | Electricity | air | PVAV Reheat | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | nonres_med | AirSourceHeatPump | Electricity | air | PVAV Reheat | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | nonres_lg | AirSourceHeatPump | Electricity | air | VAV Reheat | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | res_small | DistrictAmbient | DistrictAmbient | air | Water Source Heat Pumps with ERVs | HeatPump |  | HeatPump
Any | res_med | DistrictAmbient | DistrictAmbient | air | Water Source Heat Pumps with DOAS | HeatPump |  | HeatPump
Any | nonres_small | DistrictAmbient | DistrictAmbient | air | PVAV Reheat | HeatPump |  | HeatPump
Any | nonres_med | DistrictAmbient | DistrictAmbient | air | PVAV Reheat | HeatPump | HeatPump | HeatPump
Any | nonres_lg | DistrictAmbient | DistrictAmbient | air | VAV Reheat | HeatPump | HeatPump | HeatPump
Any | res_small | NaturalGas | DistrictCooling | air | PSZ-AC | NaturalGas |  | DistrictCooling
Any | res_med | NaturalGas | DistrictCooling | air | PSZ-AC | NaturalGas |  | DistrictCooling
Any | nonres_small | NaturalGas | DistrictCooling | air | PSZ-AC | NaturalGas |  | DistrictCooling
Any | nonres_med | NaturalGas | DistrictCooling | air | PVAV Rheat | NaturalGas | NaturalGas | DistrictCooling
Any | nonres_lg | NaturalGas | DistrictCooling | air | VAV Reheat | NaturalGas | NaturalGas | DistrictCooling
Any | res_small | Electricity | DistrictCooling | air | PSZ-AC | Electricity |  | DistrictCooling
Any | res_med | Electricity | DistrictCooling | air | PSZ-AC | Electricity |  | DistrictCooling
Any | nonres_small | Electricity | DistrictCooling | air | PSZ-AC | Electricity |  | DistrictCooling
Any | nonres_med | Electricity | DistrictCooling | air | PVAV Rheat | Electricity | Electricity | DistrictCooling
Any | nonres_lg | Electricity | DistrictCooling | air | VAV Reheat | Electricity | Electricity | DistrictCooling
Any | res_small | DistrictHeating | DistrictCooling | air | PSZ-AC | DistrictHeating |  | DistrictCooling
Any | res_med | DistrictHeating | DistrictCooling | air | PSZ-AC | DistrictHeating |  | DistrictCooling
Any | nonres_small | DistrictHeating | DistrictCooling | air | PSZ-AC | DistrictHeating | DistrictHeating | DistrictCooling
Any | nonres_med | DistrictHeating | DistrictCooling | air | PVAV Rheat | DistrictHeating | DistrictHeating | DistrictCooling
Any | nonres_lg | DistrictHeating | DistrictCooling | air | VAV Reheat | DistrictHeating | DistrictHeating | DistrictCooling
Any | res_small | AirSourceHeatPump | DistrictCooling | air | PSZ-AC | AirSourceHeatPump |  | DistrictCooling
Any | res_med | AirSourceHeatPump | DistrictCooling | air | PSZ-AC | AirSourceHeatPump |  | DistrictCooling
Any | nonres_small | AirSourceHeatPump | DistrictCooling | air | PSZ-AC | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling
Any | nonres_med | AirSourceHeatPump | DistrictCooling | air | PVAV Rheat | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling
Any | nonres_lg | AirSourceHeatPump | DistrictCooling | air | VAV Reheat | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling
Any | res_med | NaturalGas | Electricity | hydronic | Fan Coil with DOAS | NaturalGas |  | Electricity
Any | nonres_small | NaturalGas | Electricity | hydronic | Fan Coil with DOAS | NaturalGas | NaturalGas | Electricity
Any | nonres_med | NaturalGas | Electricity | hydronic | Fan Coil with DOAS | NaturalGas | NaturalGas | Electricity
Any | nonres_lg | NaturalGas | Electricity | hydronic | Fan Coil with DOAS | NaturalGas | NaturalGas | Electricity
Any | res_small | Electricity | Electricity | hydronic | Ground Source Heat Pumps with ERVs | Electricity |  | Electricity
Any | res_med | Electricity | Electricity | hydronic | Ground Source Heat Pumps with DOAS | Electricity |  | Electricity
Any | nonres_small | Electricity | Electricity | hydronic | Ground Source Heat Pumps with DOAS | Electricity |  | Electricity
Any | nonres_med | Electricity | Electricity | hydronic | Ground Source Heat Pumps with DOAS | Electricity | Electricity | Electricity
Any | nonres_lg | Electricity | Electricity | hydronic | Ground Source Heat Pumps with DOAS | Electricity | Electricity | Electricity
Any | res_small | DistrictHeating | Electricity | hydronic | Fan Coil with DOAS | DistrictHeating |  | Electricity
Any | res_med | DistrictHeating | Electricity | hydronic | Fan Coil with DOAS | DistrictHeating |  | Electricity
Any | nonres_small | DistrictHeating | Electricity | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | Electricity
Any | nonres_med | DistrictHeating | Electricity | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | Electricity
Any | nonres_lg | DistrictHeating | Electricity | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | Electricity
Any | res_small | AirSourceHeatPump | Electricity | hydronic | Fan Coil with DOAS | AirSourceHeatPump |  | Electricity
Any | res_med | AirSourceHeatPump | Electricity | hydronic | Fan Coil with DOAS | AirSourceHeatPump |  | Electricity
Any | nonres_small | AirSourceHeatPump | Electricity | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | nonres_med | AirSourceHeatPump | Electricity | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | nonres_lg | AirSourceHeatPump | Electricity | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | Electricity
Any | res_small | DistrictAmbient | DistrictAmbient | hydronic | Water Source Heat Pumps with ERVs | HeatPump |  | HeatPump
Any | res_med | DistrictAmbient | DistrictAmbient | hydronic | Water Source Heat Pumps with DOAS | HeatPump |  | HeatPump
Any | nonres_small | DistrictAmbient | DistrictAmbient | hydronic | Water Source Heat Pumps with DOAS | HeatPump | HeatPump | HeatPump
Any | nonres_med | DistrictAmbient | DistrictAmbient | hydronic | Water Source Heat Pumps with DOAS | HeatPump | HeatPump | HeatPump
Any | nonres_lg | DistrictAmbient | DistrictAmbient | hydronic | Water Source Heat Pumps with DOAS | HeatPump | HeatPump | HeatPump
Any | res_med | NaturalGas | DistrictCooling | hydronic | Fan Coil with DOAS | NaturalGas |  | DistrictCooling
Any | nonres_small | NaturalGas | DistrictCooling | hydronic | Fan Coil with DOAS | NaturalGas |  | DistrictCooling
Any | nonres_med | NaturalGas | DistrictCooling | hydronic | Fan Coil with DOAS | NaturalGas | NaturalGas | DistrictCooling
Any | nonres_lg | NaturalGas | DistrictCooling | hydronic | Fan Coil with DOAS | NaturalGas | NaturalGas | DistrictCooling
Any | res_med | Electricity | DistrictCooling | hydronic | Fan Coil with ERVs | Electricity |  | DistrictCooling
Any | nonres_small | Electricity | DistrictCooling | hydronic | Fan Coil with DOAS | Electricity |  | DistrictCooling
Any | nonres_med | Electricity | DistrictCooling | hydronic | Fan Coil with DOAS | Electricity | Electricity | DistrictCooling
Any | nonres_lg | Electricity | DistrictCooling | hydronic | Fan Coil with DOAS | Electricity | Electricity | DistrictCooling
Any | res_small | DistrictHeating | DistrictCooling | hydronic | Fan Coil with ERVs | DistrictHeating |  | DistrictCooling
Any | res_med | DistrictHeating | DistrictCooling | hydronic | Fan Coil with DOAS | DistrictHeating |  | DistrictCooling
Any | nonres_small | DistrictHeating | DistrictCooling | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | DistrictCooling
Any | nonres_med | DistrictHeating | DistrictCooling | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | DistrictCooling
Any | nonres_lg | DistrictHeating | DistrictCooling | hydronic | Fan Coil with DOAS | DistrictHeating | DistrictHeating | DistrictCooling
Any | res_small | AirSourceHeatPump | DistrictCooling | hydronic | Fan Coil with ERVs | AirSourceHeatPump |  | DistrictCooling
Any | res_med | AirSourceHeatPump | DistrictCooling | hydronic | Fan Coil with DOAS | AirSourceHeatPump |  | DistrictCooling
Any | nonres_small | AirSourceHeatPump | DistrictCooling | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling
Any | nonres_med | AirSourceHeatPump | DistrictCooling | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling
Any | nonres_lg | AirSourceHeatPump | DistrictCooling | hydronic | Fan Coil with DOAS | AirSourceHeatPump | AirSourceHeatPump | DistrictCooling

## Size Category
Size Categorization
Template | Building Category | Minimum Floors | Maximum Floors | Minimum Area | Maximum Area | Size Category
Any | Residential | 0 | 3 | 0 | 99999999 | res_small
Any | Residential | 3 | 999 | 0 | 99999999 | res_med
Any | Nonresidential | 0 | 3 | 0 | 75000 | nonres_small
Any | Nonresidential | 4 | 5 | 0 | 75000 | nonres_med
Any | Nonresidential | 0 | 5 | 75000 | 150000 | nonres_med
Any | Nonresidential | 0 | 999 | 150000 | 99999999 | nonres_lg
Any | Nonresidential | 6 | 999 | 0 | 99999999 | nonres_lg

## Lookups
These lookups are used to help users avoid input mistakes on other tabs. Please do not edit or delete existing entries or rename tables. You may add entries at the bottom of the list, but please avoid near-duplicates.
Intended Surface Type Lookup | Standards Construction Type Lookup | Building Type Lookup | Space Type Lookup | Lighting Standards Lookup | Ventilation Standards Lookup | Material Type Lookup | Construction Category Lookup | Orientation Lookup
Name | Name | Name | Name | Name | Name | Name | Name | Name
AtticFloor | Mass | FullServiceRestaurant | Anesthesia | ASHRAE 90.1-1999 | ASHRAE 62.1-1999 | StandardOpaqueMaterial | Nonresidential | North
AtticWall | SteelFramed | Hospital | Apartment | ASHRAE 90.1-2001 | ASHRAE 62.1-2004 | AirGap | Residential | NonNorth
AtticRoof | WoodFramed | LargeHotel | Apartment_topfloor_WE | ASHRAE 90.1-2004 | ASHRAE 62.1-2007 | StandardGlazing | Semiheated
DemisingFloor | IEAD | MidriseApartment | Apartment_topfloor_NS | ASHRAE 90.1-2007 | GGHC v2.2 | MasslessOpaqueMaterial | Adiabatic
DemisingWall | View | HighriseApartment | Attic | ASHRAE 189.1-2009 | AIA 2001 | SimpleGlazing | HighriseResidential
DemisingRoof | Daylight | Office | Auditorium | ASHRAE 90.1-2010 | DOE Ref Pre-1980 | Gas | Any
ExteriorFloor | Swinging | Outpatient | Back_Space | ASHRAE 90.1-2013 | DOE Ref 1980-2004
ExteriorWall | NonSwinging | PrimarySchool | Banquet | DOE Ref Pre-1980
ExteriorRoof | Heated | QuickServiceRestaurant | Basement | DOE Ref 1980-2004
ExteriorWindow | Unheated | Retail | BioHazard | GGHC v2.2
ExteriorDoor | RollUp | SecondarySchool | BreakRoom | OEESC 2014
GlassDoor | Sliding | SmallHotel | Bulk | NREL ZNE Ready 2017
GroundContactFloor | Metal | StripMall | Cafe | ZE AEDG Multifamily
GroundContactWall | Nonmetal framing (all) | SuperMarket | Cafeteria
GroundContactRoof | Metal framing (curtainwall/storefront) | Warehouse | ComputerRoom
InteriorFloor | Metal framing (entrance door) | SmallOffice | Classroom
InteriorWall | Metal framing (all other) | MediumOffice | CleanWork
InteriorCeiling | Metal Building | LargeOffice | ClosedOffice
InteriorPartition | Attic and Other | SmallDataCenterLowITE | Conference
InteriorWindow | Glass with Curb | SmallDataCenterHighITE | Corridor
InteriorDoor | Plastic with Curb | LargeDataCenterLowITE | Corridor2
OverheadDoor | Without Curb | LargeDataCenterHighITE | Corridor_topfloor
Skylight |  | Laboratory | Deli/Bakery
TubularDaylightDome |  | Automotive facility | Dining
TubularDaylightDiffuser |  | Convention centre | DressingRoom
|  | Courthouse | DryStorage
|  | Dining - bar/lounge | Elec/MechRoom
|  | Dining - cafeteria | ElevatorPumpRoom
|  | Dining - family | ElevatorCore
|  | Dormitory | ElevatorCore4
|  | Exercise centre | Entry
|  | Fire station | Equipment corridor
|  | Gymnasium | ER_Exam
|  | Health-care clinic | ER_NurseStn
|  | Library | ER_Trauma
|  | Manufacturing facility | ER_Triage
|  | Motel | Exam
|  | Motion picture theatre | Exercise
|  | Multi-unit residential | Fine
|  | Museum | GuestLounge
|  | Parking garage | GuestRoom
|  | Penitentiary | GuestRoom123Occ
|  | Performing arts theatre | GuestRoom123Vac
|  | Police station | GuestRoom2
|  | Post office | GuestRoom3
|  | Religious | GuestRoom4
|  | Retail | GuestRoom4Occ
|  | School/university | GuestRoom4Vac
|  | Sports arena | Gym
|  | Town hall | Hall
|  | Transportation | Hall_infil
|  | Warehouse | ICU_NurseStn
|  | Workshop | ICU_Open
|  | Space Function | ICU_PatRm
|  | Warehouse - refrigerated | IT_Room
|  | SmallOfficeDetailed | Janitor
|  | MediumOfficeDetailed | Kitchen
|  | LargeOfficeDetailed | Lab
|  | College | Lab with fume hood
Laundry
Library
Lobby
LockerRoom
Lounge
Mechanical
MedGas
Meeting
MRI
MRI_Control
NurseStation
NurseStn
HospitalOfficeFlr1
HospitalOfficeFlr5
OutpatientFloor2Work
Office
OpenOffice
Open lab
OR
PACU
PatCorridor
PatRoom
PhysicalTherapy
PhysTherapy
Plenum
Point_of_Sale
PreOp
PrintRoom
ProcedureRoom
PublicRestroom
Radiology
Restroom
Retail
Retail2
Core_Retail
Front_Retail
Sales/Produce
Soil Work
StaffLounge
Stair
Stair4
StandaloneDataCenter
Storage
Storage4Front
Storage4Rear
Toilet
Vending
WholeBuilding
WholeBuilding - Lg Office-basement
WholeBuilding - Lg Office-others
WholeBuilding - Lg Office
WholeBuilding - Md Office
WholeBuilding - Sm Office
Xray
Undeveloped
Reception
Dwelling Unit(s)
Atrium - H < 13m
Atrium - H > 13m
Audience - auditorium
Audience - performance arts
Audience - motion picture
Classroom/lecture/training
Conf./meet./multi-purpose
Corr. >= 2.4m wide
Corr. < 2.4m wide
Dining - bar lounge/leisure
Dining - family space
Dining - other
Dress./fitt. - performance arts
Electrical/Mechanical
Food preparation
Food preparation
Food preparation - vented
Lab - classrooms
Lab - research
Lobby - elevator
Lobby - performance arts
Lobby - motion picture
Lobby - other
Locker room
Lounge/recreation
Office - enclosed
Office - open plan
Sales area
Stairway
Storage area
Washroom
Workshop space
Automotive - repair
Bank - banking and offices
Convention centre - audience
Convention centre - exhibit
Courthouse - courtroom
Courthouse - cell
Courthouse - chambers
Penitentiary - audience
Penitentiary - classroom
Penitentiary - dining
Dormitory - living quarters
Fire station - engine room
Fire station - quarters
Gym - fitness
Gym - audience
Gym - play
Hospital corr. >= 2.4m
Hospital corr. < 2.4m
Hospital - emergency
Hospital - exam
Hospital - laundry/washing
Hospital - lounge/recreation
Hospital - medical supply
Hospital - nursery
Hospital - nurses' station
Hospital - operating room
Hospital - patient room
Hospital - pharmacy
Hospital - physical therapy
Hospital - radiology/imaging
Hospital - recovery
Hotel/Motel - dining
Hotel/Motel - rooms
Hotel/Motel - lobby
Hway lodging - dining
Hway lodging - rooms
Library - cataloging
Library - reading
Library - stacks
Mfg - corr. >= 2.4m
Mfg - corr. < 2.4m
Mfg - detailed
Mfg - equipment
Mfg - bay H > 15m
Mfg - 7.5 <= bay H <= 15m
Mfg - bay H < 7.5m
Museum - exhibition
Museum - restoration
Parking garage space
Post office sorting
Religious - audience
Religious - fellowship hall
Religious - pulpit/choir
Retail - dressing/fitting
Retail - mall concourse
Retail - sales
Sports arena - audience
Sports arena - court c4
Sports arena - court c3
Sports arena - court c2
Sports arena - court c1
Sports arena - ring
Strip mall - type 0A
Strip mall - type 0B
Strip mall - type 1
Strip mall - type 2
Strip mall - type 3
Transp. baggage
Transp. seating
Transp. concourse
Transp. counter
Warehouse - fine
OfficeLarge Data Center
OfficeLarge Main Data Center
- undefined -sch-*
Corr. >= 2.4m wide-sch-*
Corr. < 2.4m wide-sch-*
Electrical/Mechanical-sch-*
Locker room-sch-*
Stairway-sch-*
Washroom-sch-*
Hospital corr. >= 2.4m-sch-*
Hospital corr. < 2.4m-sch-*
Mfg - corr. >= 2.4m-sch-*
Mfg - corr. < 2.4m-sch-*
- undefined -sch-A
Corr. >= 2.4m wide-sch-A
Corr. < 2.4m wide-sch-A
Electrical/Mechanical-sch-A
Locker room-sch-A
Stairway-sch-A
Washroom-sch-A
Hospital corr. >= 2.4m-sch-A
Hospital corr. < 2.4m-sch-A
Mfg - corr. >= 2.4m-sch-A
Mfg - corr. < 2.4m-sch-A
- undefined -sch-B
Corr. >= 2.4m wide-sch-B
Corr. < 2.4m wide-sch-B
Electrical/Mechanical-sch-B
Locker room-sch-B
Stairway-sch-B
Washroom-sch-B
Hospital corr. >= 2.4m-sch-B
Hospital corr. < 2.4m-sch-B
Mfg - corr. >= 2.4m-sch-B
Mfg - corr. < 2.4m-sch-B
- undefined -sch-C
Corr. >= 2.4m wide-sch-C
Corr. < 2.4m wide-sch-C
Electrical/Mechanical-sch-C
Locker room-sch-C
Stairway-sch-C
Washroom-sch-C
Hospital corr. >= 2.4m-sch-C
Hospital corr. < 2.4m-sch-C
Mfg - corr. >= 2.4m-sch-C
Mfg - corr. < 2.4m-sch-C
- undefined -sch-D
Corr. >= 2.4m wide-sch-D
Corr. < 2.4m wide-sch-D
Electrical/Mechanical-sch-D
Locker room-sch-D
Stairway-sch-D
Washroom-sch-D
Hospital corr. >= 2.4m-sch-D
Hospital corr. < 2.4m-sch-D
Mfg - corr. >= 2.4m-sch-D
Mfg - corr. < 2.4m-sch-D
- undefined -sch-E
Corr. >= 2.4m wide-sch-E
Corr. < 2.4m wide-sch-E
Electrical/Mechanical-sch-E
Locker room-sch-E
Stairway-sch-E
Washroom-sch-E
Hospital corr. >= 2.4m-sch-E
Hospital corr. < 2.4m-sch-E
Mfg - corr. >= 2.4m-sch-E
Mfg - corr. < 2.4m-sch-E
- undefined -sch-F
Corr. >= 2.4m wide-sch-F
Corr. < 2.4m wide-sch-F
Electrical/Mechanical-sch-F
Locker room-sch-F
Stairway-sch-F
Washroom-sch-F
Hospital corr. >= 2.4m-sch-F
Hospital corr. < 2.4m-sch-F
Mfg - corr. >= 2.4m-sch-F
Mfg - corr. < 2.4m-sch-F
- undefined -sch-G
Corr. >= 2.4m wide-sch-G
Corr. < 2.4m wide-sch-G
Electrical/Mechanical-sch-G
Locker room-sch-G
Stairway-sch-G
Washroom-sch-G
Hospital corr. >= 2.4m-sch-G
Hospital corr. < 2.4m-sch-G
Mfg - corr. >= 2.4m-sch-G
Mfg - corr. < 2.4m-sch-G
- undefined -sch-H
Corr. >= 2.4m wide-sch-H
Corr. < 2.4m wide-sch-H
Electrical/Mechanical-sch-H
Locker room-sch-H
Stairway-sch-H
Washroom-sch-H
Hospital corr. >= 2.4m-sch-H
Hospital corr. < 2.4m-sch-H
Mfg - corr. >= 2.4m-sch-H
Mfg - corr. < 2.4m-sch-H
- undefined -sch-I
Corr. >= 2.4m wide-sch-I
Corr. < 2.4m wide-sch-I
Electrical/Mechanical-sch-I
Locker room-sch-I
Stairway-sch-I
Washroom-sch-I
Hospital corr. >= 2.4m-sch-I
Hospital corr. < 2.4m-sch-I
Mfg - corr. >= 2.4m-sch-I
Mfg - corr. < 2.4m-sch-I
- undefined -
Storage area - refrigerated
Warehouse - fine - refrigerated
Warehouse - med/blk - refrigerated
Warehouse - med/blk2 - refrigerated
Return Plenum
Deli
Bakery
Vestibule
Produce
Sales
MediumOffice - Storage
MediumOffice - Stair
MediumOffice - OpenOffice
MediumOffice - Lobby
MediumOffice - Elec/MechRoom
MediumOffice - Corridor
MediumOffice - ClosedOffice
MediumOffice - Conference
MediumOffice - BreakRoom
MediumOffice - Dining
MediumOffice - Classroom
MediumOffice - Restroom
SmallOffice - Storage
SmallOffice - Stair
SmallOffice - OpenOffice
SmallOffice - Lobby
SmallOffice - Elec/MechRoom
SmallOffice - Corridor
SmallOffice - ClosedOffice
SmallOffice - Conference
SmallOffice - BreakRoom
SmallOffice - Dining
SmallOffice - Classroom
SmallOffice - Restroom
SmallOffice - Attic
Courthouse - Break Room
Courthouse - Cell
Courthouse - Conference
Courthouse - Corridor
Courthouse - Courtroom
Courthouse - Courtroom Waiting
Courthouse - Elevator Lobby
Courthouse - Elevator Shaft
Courthouse - Entrance Lobby
Courthouse - Judges Chamber
Courthouse - Jury Assembly
Courthouse - Jury Deliberation
Courthouse - Library
Courthouse - Office
Courthouse - Parking
Courthouse - Plenum
Courthouse - Restrooms
Courthouse - Security Screening
Courthouse - Service Shaft
Courthouse - Stairs
Courthouse - Storage
Courthouse - Utility
College - Conference
College - Corridor
College - Elevator Shaft
College - Entrance Lobby
College - Lounge
College - Office
College - Restroom
College - Utility
College - Art Classroom
College - Classroom
College - Laboratory
College - Lecture Hall
College - Media Center
College - Stairs
College - Storage